## Registry Inf - for each PMU
Phasor Measurement Unit
PJM Registry Information -- To be filled per Phasor Measurement Unit
| Entry Type | Value | PJM Comment | TO Comment
Location | Company Name: |  | Maximum 50 Characters
ISO/RTO Name:
| Substation/Plant Name: |  | Maximum 50 Characters
| Substation/Plant location: Latitude – Longitude:: |  | Maximum 15 Characters
| Time Zone |  | Time Zone of the Substation. This is different than the data time stamp which for PJM project is in UTC
Contact Information for Phasor Data:
o Name
o Phone
o Email
Phasor Measurement Unit Information | PMU IDCODE |  | As per assigned IDs; see 'ID Code assignment' worksheet for the IDs available for your company's PMU/PDCs
| PMU In Service Date |  | mm/dd/yyyy
| STN |  | Maximum 16 Characters; As defined in 'STN and CHNAM' work sheet in this excel file
| PMU Manufacturer |  | Maximum 50 Characters
| PMU Model (Name and Version) |  | Maximum 35 Characters
| PMU Firmware Version |  | Maximum 15 Characters
| PMU Class |  | 'P' or 'M' (2011 std.) or '0' or '1' (2005 std.)
| PMU Reporting Rate |  | Reporting Rate
| PMU Operational Status |  | Free form For Example: In Service, On Outage, Not Connected to PDC, In Testing. Maximum 35 Characters
Time Synchronization Source (for the PMU):
| o Manufacturer |  | Maximum 50 Characters
| o Model (Name and/or Version) |  | Maximum 35 Characters
Data Sent to - from this PMU (To be repeated for each PDC ):
| o PDC (ID Code) |  | As per assigned IDs; see 'ID Code assignment' worksheet for the IDs available for your company's PMU/PDCs
| o PDC Type |  | Substation or Regional or Central (Main)
Voltage Phasor Measurements (To be repeated for each voltage phasor measurement) | CHNAM |  | Maximum 16 Characters defined as per specifications on sheet 'STN and CHNAM'
| Data Representation (Polar or Rectangular) |  | PJM prefers Polar representation
| Data Format (Integer or Floating Point) |  | PJM prefers Integer format
If Line Side Measurement:
| o Line Identifier |  | Free form field. Could be a description or the ID used by the TO to identify the line when the voltage source is on the line side
| Breaker #1 Identifier |  | Free form field. Could be a description or the ID used by the TO to identify the Breaker
Breaker #2 Identifier
If Bus Side Measurement:
| o Bus Identifier |  | Free form field. Could be a description or the ID used by the TO to identify the Bus if the Voltage source is on the Bus side
| Nominal Voltage |  | For Example: 138 KV or 230 KV or 345 KV or500 KV
Instrument Transformer:
o Device Description
o Accuracy Class
o Ratio
| Phasor relation to reference phasor (Due to Δ-Y) |  | This would be applicable to 25 KV / 23 KV / 12.5KV systems
Measurement adjustments required (external to PMU):
| o Scaling Factors |  | Free Form Field: to identify if there are any scaling adjustments to be done to the measurements. In most cases this should be not applicable
| o Phasor angle adjustment |  | Free Form Field: to identify if there are any phase angle adjustments to be done to the measurements. In most cases this should be not applicable
Current Phasor Measurements (To be repeated for each current phasor measurement) | CHNAM |  | Maximum 16 Characters defined as per specifications on sheet 'STN and CHNAM'
| Data Representation (Polar or Rectangular) |  | PJM prefers Polar representation
| Data Format (Integer or Floating Point) |  | PJM prefers Integer format
| Line Identifier |  | Free form field. Could be a description or the ID used by the TO to identify the line
| Breaker #1 Identifier |  | Free form field. Could be a description or the ID used by the TO to identify the Breaker
| Breaker #2 Identifier |  | Free form field. Could be a description or the ID used by the TO to identify the Breaker
| Nominal Voltage |  | For Example: 138 KV or 230 KV or 345 KV or500 KV
Instrument Transformers (Rows 58 to 61 shall be repeated for each transformer):
o Device Description
o Accuracy Class
o Ratio
| Phasor relation to reference phasor (Due to Δ-Y) |  | This would be applicable to 25 KV / 23 KV / 12.5KV systems
Measurement adjustments required (external to PMU):
| o Scaling Factors |  | Free Form Field: to identify if there are any scaling adjustments to be done to the measurements. In most cases this should be not applicable
| o Phasor Angle Adjustment |  | Free Form Field: to identify if there are any phase angle adjustments to be done to the measurements. In most cases this should be not applicable
Analog Measurements (To be repeated for each analog measurement; Name any additional analog measurements other than the phasors (listed above) that this PMU is providing. For example: Instantaneous current, Instantaneous voltage, Temperature) | CHNAM |  | Maximum 16 Characters defined as per specifications on sheet 'STN and CHNAM'
| Name of Analog provided |  | Free Form Text.
Digital Measurements (To be repeated for each digital measurement. For example: Breaker Status, Control System Status Flags) | CHNAM |  | Maximum 16 Characters defined as per specifications on sheet 'STN and CHNAM'
Digital Data Information:
| o Identifier |  | Free form field. In case of breakers this field could be the ID used by the TO to identify the Breaker
| o Description of the digital data provided |  | Free-form Description. For Example entry could look like: "Breaker Status; 1 = Closed, 0 = Open"
Local (Substation) Archive | Archive Description |  | Free Form text
| Archival Rate |  | Free Form text
| Archival Format |  | Free Form text
| Data Retention Period in days |  | Free Form text

## Registry Inf - for each PDC
Phasor Data Concentrator (PDC)
PJM Registry Information -- To be filled per Phasor Data Concentrator
| Entry Type | Value | PJM Comment | TO Comment
Location | Company Name: |  | Maximum 50 Characters
ISO/RTO Name:
| PDC Location (Substation/Plant Name for Substation PDC or Control Center Name for Central PDC): |  | Maximum 50 Characters
| Substation/Plant location (if this is a Substation PDC): Latitude – Longitude:: |  | Maximum 15 Characters
| Time Zone |  | Time Zone of the Substation. This is different than the data time stamp which for PJM project is in UTC
Contact Information for PDC administrator:
o Name
o Phone
o Email
Phasor Data Concentrator (PDC) Information | PDC IDCODE |  | As per assigned IDs; see 'ID Code assignment' worksheet for the IDs available for your company's PMU/PDCs
| PDC Vendor |  | Maximum 50 Characters
| PDC Firmware Version |  | Maximum 15 Characters
Time Synchronization Source (if used for PDC)
| o Manufacturer |  | Maximum 50 Characters
| o Model (Name and/or Version) |  | Maximum 35 Characters
| o Firmware Version |  | Maximum 15 Characters
Data Sent to (To be repeated for each PDC ):
| o PDC (ID Code) |  | As per assigned IDs; see 'ID Code assignment' worksheet for the IDs available for your company's PMU/PDCs
| o PDC Type |  | Substation or Regional or Central (Main)
Archival Information | Archive Description |  | Free Form text
| Archival Rate |  | Free Form text
| Archival Format |  | Free Form text
| Data Retention Period in days |  | Free Form text

## ID Code Assignment
Phasor Measurement Unit & Phasor Data Concentrator ID Codes To be used in Registry,Config, Command and Data Frames
|  |  |  | PJM | Jefferson PDC 23611
Company | Type | ID Codes Start | ID Code End |  | Allegheny Power (AP)
Allegheny Power (AP) | PMUs | 17001 | 17500 |  | American Electric Power (AEP)
| PDCs | 17501 | 17600 |  | Baltimore Gas & Electric Co. (BG&E)
American Electric Power (AEP) | PMUs | 17601 | 18100 |  | Commonwealth Edison (ComEd)
| PDCs | 18101 | 18200 |  | Dominion, Virginia Power (VP)
Baltimore Gas & Electric Co. (BG&E) | PMUs | 18201 | 18650 |  | Duquesne Light Co
| PDCs | 18651 | 18750 |  | First Energy
Commonwealth Edison (ComEd) | PMUs | 18751 | 19250 |  | Orange & RockLand
| PDCs | 19251 | 19350 |  | Pennsylvania Power & Light (PPL) Utilities
Dominion, Virginia Power (VP) | PMUs | 19351 | 19850 |  | Philadelphia Electric Co. (PECO)
| PDCs | 19851 | 19950 |  | Pepco Holding Inc (PHI)
Duquesne Light Co | PMUs | 19951 | 20450 |  | Public Service Electric & Gas Co (PSEG)
| PDCs | 20451 | 20550 |  | Duke Energy Ohio (DEOK)
FirstEnergy | PMUs | 20551 | 21050
| PDCs | 21051 | 21150
Orange & RockLand | PMUs | 21151 | 21250
| PDCs | 21251 | 21300
Pennsylvania Power & Light (PPL) Utilities | PMUs | 21301 | 21800
| PDCs | 21801 | 21900
Philadelphia Electric Co. (PECO) | PMUs | 21901 | 22400
| PDCs | 22401 | 22500
Pepco Holding Inc (PHI) | PMUs | 22501 | 22950
| PDCs | 22951 | 23050
Public Service Electric & Gas Co (PSEG) | PMUs | 23051 | 23500
| PDCs | 23501 | 23600
Duke Energy Ohio (DEOK) | PMUs | 23651 | 24100
| PDCs | 24101 | 24200
PJM Interconnection and Future Use | NA | 24201 | 24999

## STN and CHNAM
STN and CHNAM Nomenclature To be used in Registry and Config Frame
Station Name 16 bytes ASCII | STN | 2 Bytes Company Identifier (as defined in sheet 'Company Identifier for STN')
2 Bytes of Blank characters
9 Bytes MMWG Bus Name (Use the first nine bytes from the name of one of the highest voltage Buses within that substation. If needed fill with succeeding blanks to complete nine bytes)
1 Byte of a blank character
2 Bytes Device ID within Station
Channel Name 16 bytes ASCII | CHNAM | For all Values 1 Byte to Identify measurement: Phasor on Bus side -- B Phasor on Line side -- L Digital -- D Non-Phasor Analog -- A
For Phasor Values: 3 Byte nominal voltage of the measurement location For Non-Phasor Values: 3 Bytes of blanks
For Phasor Values: 9 Bytes of ‘To Bus MMWG Name’ or ‘Bus Section Identifier' (Use the first nine bytes from the name with succeeding blanks as needed) For Non-Phasor Values 9 Bytes of free form Identifier with succeeding blanks as needed to fill up all nine bytes
For Phasor Values: 1 Byte of Circuit number for Parallel Lines or Transformers to the same "To" Bus For Non-Phasor Values: 1 Byte of blank
2 Bytes Measurement Variable Identifier For all values: V1: Positive Sequence Voltage I1: Positive sequence Current DC: Digital Channel AC: Analog Channel (Non-Phasor)

## Company Identifier in STN
Company Identifier in STN
Identifier | Company Name
FE | ATSI (First Energy West Integration)
AA | American Electric Power (AEP)
AE | Atlantic Electric Co. (AE)
AM | Ameren Control Area
AP | Allegheny Power (AP)
CA | PJM RTO (Control Area)
DA | Dayton Power & Light
CE | Commonwealth Edison (ComEd), Northern Illinois Control Area (NICA)
CI | Cinergy
CP | CPL, CPLW
CL | Cleveland Public Power
BC | Baltimore Gas & Electric Co. (BG&E)
BR | Big Rivers Electric Corporation (BREC)
DQ | Duquesne Light Co
DP | Delmarva Power & Light Co.
DK | DUKE
DO | DEOK
EK | EKPC
EN | ENTERGY
FE | FirstEnergy
HE | HE
HQ | Hydro Quebec (HQ, SOUTHQ)
IL | Illinois Power & Light (IL)
IN | Indianapolis Power & Light Company (IPL)
IP | Illinois Power (IP)
JC | Jersey Central Power & Light (JCPL)
LG | LGE Energy (LGEE)
MI | MISO Tags
ME | Metropolitan Edison (MetEd)
MC | Mid-American Energy Co.
MX | Michigan Electric Coordinated System (MECS)
NB | New Brunswick (NENB, NB)
NX | New England Power Exchange (NEPEX)
NP | NIPSCO
NY | New York ISO/Power Pool
OH | Ontario Hydro
OV | Ohio Valley Electric Corp
PE | Philadelphia Electric Co. (PECO)
PN | Pennsylvania Electric Co (PN)
PL | PPL Electric Utilities
PP | Potomac Electric Power Co. (PEPCO)
PS | Public Service Electric & Gas Co (PSEG)
SC | SC (South Carolina)
SI | Southern Indiana Gas & Electric Company (SIGE)
TV | TVAA
UG | UGI Utilities
VP | Dominion, Virginia Power (VP)
OR | Orange and Rockland

## MMWG Bus Names in STN & CHNAM
TO | Name | MMWG Bus Name for STN | Example Pos. Seq. Values for each TO (with reference to attached images)
AEP | Amos 765 | 05AMOS | Vpos. = (V2 + a V3 + a2 V1)/3
AEP | Breed 345 | 05BREED
AEP | Canton Central 345 | 05CANTNC
AEP | Dumont 765 | 05DUMONT
AEP | Jefferson 765 | 05JEFRSO
AEP | Tristate 765 | ?
AEP | Cook 345 | 05COOK
AEP | Fostoria Central 345 | 05FOSTOR
AEP | Tanners Creek 345 | 05TANNER
AEP | Broadford 765 | 05BROADF
AEP | Conesville 345 | 05CONES
AEP | Jacksons Ferry 765 | 05J.FERR
AEP | Kammer 765 | 05KAMMER
AEP | Kanawha River 345 | 05KANAWH
AEP | Rockport 765 | 05ROCKPT
AEP | Ft. Wayne | ?
AEP | Roanoke | 05ROANO1
AEP | Canton | ?
AP | Doubs SS - 500 kV | 01DOUBS | Vpos. = (V2 + a V3 + a2 V1)/3 or (Vy + a Vz + a2 Vx)/3 or (VB + a VC+ a2 VA)/3
AP | Doubs SS - 230 kV | 01DOUBS
AP | Fort Martin SS | 01FMARTN
AP | Pruntytown SS | 01PRNTY
AP | Black Oak SS | 01BLACKO
AP | Hatfield SS | 01HATFLD
AP | Meadowbrook SS | 01MDWBRK
AP | Belmont SS | 01BELMNT
BGE | Conastone | CNASTONE | Vpos. = (VA + a VB + a2 VC)/3
BGE | Waugh Chapel | W CHAPEL
ComEd | Cherry Valley | CHERR; B | ?
ComEd | Libertyville | LIBER; B
ComEd | Nelson | NELSO; B
ComEd | Goodings Grove | GOODI; 1R
DOM | Mt. Storm | 8MT STM | Vpos. = (VC + a VA + a2 VB)/3
DOM | Lexington | 8LEXNGTN
DOM | Dooms | 8DOOMS
DOM | Morrisville | 8MORRSVL
DOM | Ladysmith | 8LDYSMTH
DOM | Bristers | 8BRISTER
DOM | Loudon | 8LOUDOUN
DOM | Elmont | 8ELMONT
DOM | Cunningham | 8CUNNING
DOM | Carson | 8CARSON
DOM | Chickahominy | 8CHCKAHM
DUQ | Collier | 15COLLIE | Vpos. = (VC + a VA + a2 VB)/3
DUQ | Crescent | 15CRESCN
FE | Keystone | KEYSTONE | Vpos. = (Vy + a Vz + a2 Vx)/3 (Penn. Elec.)
FE | TMI 500 | 3 MILE I
FE | Conemaugh | CONEM-GH
FE | Homer City | HOMER CY
FE | Erie West | ERIE W
FE | East Windsor | E WINDSR
FE | Hunterstown | HUNTERTN
PECO | Peach Bottom 500kV North | PEACHBTM | Vpos. = (VA + a VB + a2 VC)/3
PECO | Limerick 500kV | LIMERICK
PECO | Whitpain 500kV | WHITPAIN
PHI | Orchard | ORCHARD | Vpos. = (VA + a VB + a2 VC)/3 (PEPCO)
PHI | Brighton | BRIGHTON
PHI | Keeney | KEENEY
PHI | Burches Hill | BURCHES
PPL | Elimsport 230kV Sub | ELIM | Vpos. = (VA + a VB + a2 VC)/3 on 500KV & Vpos. = (VC + a VB + a2 VA)/3 on 230 KV
PPL | Brunner Island 230kV Swyd | BRIS
PPL | Martins Creek 230kV Swyd | MACR
PPL | Susquehanna 500/230kV Sub | SUSQHANA
PPL | Susquehanna 230kV Swyd | SUSQ 2
PPL | Alburtis 500kV Sub | ALBURTIS
PPL | Wescosville 500kV Sub | WESCOVLE
PPL | Lackawanna 500/230kV Sub | LACK
PPL | Juniata 500kV Sub | JUNIATA
PPL | South Akron 230kv sub | SAKR
PPL | Quarry 230kV Sub | QUAR
PPL | Frackville 230 kV Sub | FRAC
PSEG | Branchburg | BRANCHBG | Vpos. = (V1+ a V2 + a2 V3)/3
PSEG | Deans | DEANS
PSEG | Hope Creek | HOPE CRK
PSEG | New Freedom | NEW FREE
PSEG | Bayway | BAYWAY
PSEG | Belleville | BELLVLLE
PSEG | Linden | LINDEN
PSEG | Lawrence (was Trenton) | ?
PSEG | Bergen 230 | BERGEN
PSEG | Roseland | ROSELAND
PSEG | Hudson
PSEG | Waldwick | WALDWICK
RECO | South Mahwah S/S | SMAHWAH1 | ?