## Matrix
SRSTF
Proposal Development Process
Potential Component Solutions
# | Draft Design Components | Related To | Priority | NERC Standards | Meaning | Status Quo | A | B | C | D | E | F | G | H | I | I2
BLACK START AVAILABILITY
A | Ensure the future availability of critical BS |  |  | EOP-005-1, Attachment 1 Item 2 EOP-005-1 R8 EOP-005-2 R1.4 EOP-005-2 R6.1 | Transmission Operator (TOP) (a.k.a. PJM) shall verify number, size, availability and location of BS units are sufficient to meet restoration plan requirements. BS units must be able to restore cranking path and critical loads. | RFP Process administered by PJM for replacement BS (Section 10- M-14D) If no responses to RFP: Make exception to criteria; BS from other areas; Refurbishment through capital cost recovery | Include BS as a requirement for all new generation (excl wind, solar, nuclear) above x MW (200?) | Incorporate "Restoration Resource" into RTEP Planning process (BS Analysis) | Incorporate BS requirements (zonal; regional, LDA) in RPM process | Give PJM "Reliability Backstop" authority if other methods of BS acquisition fail (RMR - Like structure) | Make modifications to current procurement process to make acquisition process more flexible. | Special consideration for BS units in the generation interconnection queue process. | PJM acquire required BS in cost effective manner through a market process. (Applicable to either a Tier 1 or Tier 2)
B | Method for retention of necessary, critical BS based on restoration strategy |  |  | None |  | Cost recovery method (OATT Schedule 6A, Manual M-27, Section 7); continue one-off agreements for unit refurbishment | Consider changes to the incentive rate structure for formula rate, capital recovery, and FERC approved rates | Revise testing criteria from annual to every 3 years (match NERC) | Continue to explore other options for refurbishment process | Compensation method for BS from other zones | RMR-like structure that goes beyond 2 years and $2M | Go back to cost-based rate and add to transmission tariff rates | BS unit payment should be factored based on MW of critical load required (not ICAP) | Consider compensating fuel storage other than oil | Potential differences in compensation of Tier 1 vs Tier 2. | Have Generation Owners pay a portion of BS costs in a zone with the capability to self-supply.
C | Initial restoration assumptions (grid's starting point from the time restoration process starts) |  |  | EOP-005-2 Purpose: Ensure plans, Facilities, and personnel are prepared to enable System restoration from Blackstart Resources to assure reliability... | Ensure restoration from BS Resources to assure reliability is maintained during restoration and priority placed on restoring the Interconnection | Complete PJM blackout with no outside assistance available: Normal weather pattern, intermediate to peak load, minimal equipment damage and normal working hours. Unit time to start from the Markets database. A 16 hour fuel quantity or less based on TO requirement (see Tariff language) | Estimated time to start should not use the Markets DB data (1C) | PJM blacked out with outside assistance available (2C) | Partial PJM blacked out with internal or external assistance available (3C) | Plan for worst case, but focus training & analysis on a variety of scenarios (see C1) | [6 empty] | Include in ALL solution packages | (1C) Desire to utilize available generation data in Restoration Analysis | (2C) Option not supported by PJM members. | (3C) Option not supported by PJM members.
C1 | Additional restoration assumptions (sensitivity analysis - stage 3 input) |  |  |  |  | N/A | Consider a mix (%) of hot / cold start up times based on historical run averages (same as consider different load levels? Same as consider different LMPs?) | Consider transmission asset unavailability | Consider cyber attacks | BS unit availability | [6 empty] | Package 1
D | Restoration Time (Target) |  |  | None |  | Target time for complete EHV restoration of RTO (transmission) is 24 hours. | Target time* for complete transmission system (not load) restoration from total blackout is 48 hours. | Target time 72 hours. | Sliding restoration time based on scenario (see sheet 3) | Target time less than 24 hours. | PJM to consult with OPSI ISAC and possibly conduct a study as to what target restoration time should be in an effort to assess economic and social implications of black out. (Long-term consideration) | [5 empty] | Package 2
E | Classification of BS generators |  |  | None |  | Critical BS - compensated under OATT Sched 6A - documented in Restoration Plan Non-critical - BS might be available (no testing or compensation); BS unit must control frequency and voltage. Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource . | Develop two tiers of BS units: Tier 1 meets the same criteria as current BS units. Tier 2 BS units would have to be available within 4 hours, the timeframe needed to assist in energizing critical loads. Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource. | Same site, very small BS unit that starts a larger unit. Larger unit should be compensated as tier X BS. (1E) | Renewables (wind, solar) with consideration on how to control voltage/frequency. New resources to assist in voltage/frequency. (2E) | Investigate use of mobile BS units (2E) | MERGED WITH STATUS QUO AND "A". Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource | [5 empty] | Option dropped due to lack of support or infeasibility | (1E) Small unit would be considered BS in this case. Larger unit is cranked unit therefore no additional compensation | (2E) These options dropped as specific options as any unit that meets the BS criteria can be considered a BS unit
| BS requirements: MW Number, Availability / Redundancy, Location |  |  | EOP-005-1, Attachment 1 Item 2 EOP-005-1 R8 EOP-005-2 R1.4 EOP-005-2 R6.1 | TOP shall verify number, size, availability and location of BS units are sufficient to meet restoration plan requirements. BS units must be able to restore cranking path and critical loads.
F | Black Start MW Required |  |  | EOP-005-1 R8 EOP-005-2 R6 |  | Critical Load defined in M-36 Attachment A (Nuclear aux power, gas infrastructure power, Critical steam aux power) Ensure Reactive & Volt / VAR sufficient based on testing and simulations. Cranking path availability tested during simulations. | Carry only enough BS in an area* to start the next largest unit (continue restoration from there) (1F) | Develop Tiered BS by zone: Tier 1 = Based on load req'd for critical steam aux power (<= 90 min on-line capability) Tier 2 = Based on load req'd for nuclear aux power for safe shutdown & gas infrastructure power (<= 4 hr on-line capability) Maintain gas infrastructure and nuclear safe shutdown load as priority with 4 hour restoration target (may be met with Tier 1 BS, Tier 2 BS or non-BS Generation. Ensure Reactive & Volt / VAR sufficient based on testing and simulations. Cranking path availability tested during simulations. | Augment existing BS with new BS designed to energize EHV system (ISO-NE approach) (2F) | MERGED WITH "B". Maintain gas infrastructure and nuclear safe shutdown load as priority with 4 hour restoration target (may be met with Tier 1 BS, Tier 2 BS or non-BS Generation | NEW STATEMENT: Consider a buffer to maintain the BS requirement a % higher than Critical Load. ORIGINAL STATEMENT: "PJM specify a minimal amount of BS to handle complete blackout scenario. Tier1 BS req = 125% of Critical steam aux load (by zone)" | TO can optionally acquire additional BS if desired through bilateral contracts (outside of PJM OATT) | MERGED WITH STATUS QUO AND "B". | MERGED WITH STATUS QUO AND "B". Cranking path availability tested during simulations |  |  |  | (1F) Option not supported by PJM members (no contingency BS would be available) | (2F) PJM EHV system too widespread to consider this approach
G | Black Start Redundancy |  |  |  |  | Minimum of 3 BS units per zone (with exceptions); Restrictions of planned and maintenance outages of BS units - Rules incorporated into eDART tool - based on number of units and location. | Allow more than 3 BS units per site. | Minimum of 2 BS units per locational requirement (one resource could supply multiple locations.) | At least one BS unit per zone, if Tier 1 or Tier 2 load identified. Redundancy can be provided by other zones | Ensure not too many BS units tie to the same gas pipeline | PJM would consider fuel diversity in selection of BS units
H | Geographic / Locational Aspect of Overall Strategy |  |  | None |  | Plans based on a TO zonal basis with PJM M-36 defining common elements. Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system. | Set up Restoration "Regions" for consolidation of restoration plans (i.e.. East, West, South, etc). Where beneficial. | Develop an RTO-wide Restoration plan which focuses on restoration of EHV network (1H) | IN CONJUNCTION WITH STATUS QUO. TO Based plans but allow BS from other regions/zones. | CAPTURED WITH COMPONENT C. Have plan for worst case, but focus training/plans on more probable scenarios (i.e. partial blackout; top-down method) (2H) | IN CONJUNCTION WITH STATUS QUO. Zones may be aggregated if BS shortages exist | [6 empty] | (1H) RTO-wide restoration plan not feasible at this time due to scope of plan and control | (2H) This option is redundant to approved option D of Component C
I | Entity responsible for identification of BS quantity and location in system restoration |  |  | EOP-005-2 Applicability Section: Transmission Owners identified in the Transmission Operator's restoration plan | Ensure restoration from BS Resources to assure reliability is maintained during restoration and priority placed on restoring the Interconnection | Based on TO Restoration Plan with PJM approval. PJM, with TO input, select replacement BS through RFP process | TO identify (1I) | PJM identify with TO / REGION input | PJM identify (2I) | MERGED WITH "B". PJM with Restoration Region Input (3I) | PJM and TO's develop a joint plan. (SOS) (4I) | CAPTURED WITH COMPONENT F. TO can optionally acquire additional BS if desired through bilateral contracts (outside of PJM OATT) (5I) | [5 empty] | (1I) Option not supported by PJM members | (2I) Option not supported by PJM members | (3I) Merged with Option B | (4I) Option not supported by PJM members | (5I) Option is redundant with Option F of component F
Note on L14: Chantal-Aimee Hendrzak: Need more details

## Parking Lot
# | Parking Lot Items | Complete?
1 | Consideration of BS in the RTEP process and the implications of that
2 | Timing of zonal restoration; no zone left behind | x
3 | How do we establish availability today for BS? | x
4 | Consideration of the changing loads (sensitivity), terrorism, generation types
5 | Quantify economic impact of a blackout. Find studies.
6 | Third party input into B/S criteria
7 | Produce diagram based on different definitions of tier 2 units (tier 2 versus tier X) | x
8 | Define critical BS versus non-critical BS and tier X non-critical BS | x
9 | Share results of EPRI Restoration study once complete
10 | Document impact to PJM staff with regard to strategy chosen.

## Restoration Time Idea (hidden)
| Complete RTO Blackout with no outside assistance available | Complete RTO Blackout with outside assistance available | Partial RTO Blackout (internal and external assistance available)
Restoration Target Time | 72 hours | 24 hours | 4-24 hours (depending on situation)

## Interests
Initial SRSTF Stakeholder Interests:
1) Concern that existing Black Start procurement and compensation methods are not attracting or maintaining Black Start units. Need an improved method of acquiring/incenting Black Start units. (13 mentions)
2) Restoration plan must include sufficient redundancy of Black Start resources to allow for flexibility and contingency planning. (6 mentions)
3) Interest in maintaining or improving overall restoration target time (currently 24 hours). (4 mentions)
4) Task force should develop a long term solution with the recognition that we may need a short term solution until we get there. (4 mentions)
5) Investigate alternative restoration approaches, i.e. top-down from restoration perspective of restoring high voltage system first, bottom-up approach where low voltage is restored first, RTO-wide approach where PJM indentifies how to restore the system versus local restoration plans, interregional pooling of Black Start resources. (4 mentions)
6) Sense of urgency to complete task force recommendations. (3 mentions)
7) Continue to meet NERC and NRC standards. (3 mentions)
8) Clarity for rules of defining critical Black Start units with PJM in control of process. (4 mentions)
9) Keep restoration plans on a TO zonal level (i.e. status quo). (2 mentions)
10) Black Start procurement should NOT be market based solution. (2 mentions)
11) Interest in waivers for environmental restrictions during system restoration scenarios. (2 mentions)
12) Allocation of CIP related costs along cranking paths for interregional approach. (2 mentions)
13) Set and communicate, externally to States as well for example, a clear Restoration objective (load restoration priority, restoration time, communication requirements, zonal generation mix, regulatory or public expectations, etc). (3 mentions)
Additional Interests that only got one mention:
1) Black Start procurement should be market based solution.
2) Emphasis on generators to have their own Black Start.
3) Individual zones are brought back in a manner where all receive some amount of load/supply restoration during the ramp up such that no zone would be "the last zone" to be restored. (Comparability/relative equity of restoration times)
4) Solution should be cost effective.
5) PJM to assist in defining quantity of Black Start resources needed.
6) Leverage the success of the local approach in the restoration plan in whatever solution is identified going forward. New plan needs to be, at minimum, better than current approach.
7) Create an economic metric by which any new Black Start Strategy can be assessed, in combination with established NERC and NRC standards, so that the costs and benefits of a new strategy can be compared. (Cost justification)

## Package Solutions
SRSTF
SOLUTION DETAILS
Instructions: Complete this form as needed. Potential solutions should be populated from the Proposal Matrix
Package Solutions2
|  | Status Quo | Package 1 | Package 1A | Package 2 | Package 2A | Package 2B | Package 2C | Package 3 | Package 3A | Package 4 | Package 5 | PJM - IMM Proposal
1 | Restoration Time (Target) | 24 hours |  |  | 48 hours |  | Sliding Restoration Time based on Scenario (72 hours for complete blackout with no outside help) | 48 hours | Based on target anywhere from 24-48hrs |  | No time goal; conditions-based restoration
2 | Redundancy | Minimum of 3 Units Per Zone ( with Exceptions) |  |  | Minimum one BS unit per Zone |  |  | Minimum of 3 BS units per zone (with Exceptions) | Minimum of 2 BS unit per Zone (with Exceptions) |  | Minimum of one BS unit per Region | Minimum of one BS unit per Zone regardless of critical load and a Minimum of 2 units per aggrgated zone Explanantion: Each TO should have a black start unit to participate in aggrgate zone black start. The gen could also be used to serve some important loads in cities. Redundancy would be accompished with neighbors' help. | Minimum of 2 BS allocated to each zone with a Critical Load Requirement (with Exceptions)
3 | Geography | TO zone |  | Zones may be aggregated if BS shortages exist | Zones may be aggregated if BS shortages exist |  | Set up Restoration "Regions" for consolidation of restoration plans (i.e. East, West, South, etc) where beneficial | TO Zone | Zones may be aggregated if BS shortages exist |  | Set up Restoration "Regions" for consolidation of restoration plans (i.e. East, West, South, etc) where beneficial | Zones may be aggregated if BS shortages exist | Proactive approach to identifying areas of the system where it would be beneficial to aggregate TO Restoration plans
4 | Entity responsible for BS location | TO; with PJM approval |  | PJM with TO Input | PJM; with TO input | TO, with PJM input | PJM; with TO input | TO, with PJM input | TO, with PJM approval | PJM with TO input
5 | Critical Black Start Compensation Outlined | Critical BS (OATT Sched 6A), 13 month test required |  |  | Tier 1: Critical BS (OATT Sched 6A), 13 month test required / Tier 2: Compensation would need to be developed. | [5 empty] | Critical BS (OATT Sched 6A), 13 month test required | Tier 1: Critical BS (OATT Sched 6A), 13 month test required / Tier 2: Compensation would need to be developed. | Critical BS (OATT Sched 6A), 13 month test required
6 | Tiered Approach ? | Tier 1 only; 90 minutes close to a dead bus |  |  | Keep existing Tier 1 BS (90 minute start); Establish Tier 2 BS (same requirements as Tier 1 but a 4 hour start) | [5 empty] | Tier 1 only; 90 minutes close to a dead bus | Keep existing Tier 1 BS (90 minute start); Establish Tier 2 BS (same requirements as Tier 1 but a 4 hour start) | Revise existing requirement of 90 minute start time for BS resources to four hours or less (with exceptions)
8 | Amount of black start MW required | Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load + margin on a zonal level | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin) + nuclear safe shutdown power + gas infrastructure load |  | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1, Tier 2 or non-BS) |  |  | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin + nuclear safe shutdown power + gas infrastructure load | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1 or Tier 2) |  | Based on PJM analysis of available resources (generation, transmission) | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1 or Tier 2) | (Aux power for all generation that can be restored in four hours + nuclear safe shutdown power + gas infrastructure load) * 110%
9 | Initial Restoration: Clear Assumption on Outside Assistance (Design Comp C) | Complete PJM blackout with no outside assistance available: working hours.
10 | Initial Restoration: Weather/Load (Design Comp C) | Normal weather pattern, intermediate to peak load, minimal equipment damage and Hot Unit time to start from the Markets database. (Time to start is Notification time + Hot Startup time) | [10 empty] | Normal weather pattern, intermediate to peak load, minimal equipment damage and Hot Unit Start time from the Markets database.
16 | Scenarios in Restoration Drills (Design Comp C) | Plan for worst case, but focus training & analysis on a variety of scenarios
12 | Area for Restoration Assumption (Design Comp H) | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  |  |  | Plans based on "Restoration Regions" | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  | Plans based on "Restoration Regions" | Plans based on a TO zonal basis with PJM M-36 defining common elements. | Proactive approach to identifying areas of the system where it would be beneficial to aggregate TO Restoration plans; M-36 defining common elements
13 | Responsibility for Restoration and coordination (Design Comp H) | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system. | [8 empty] | Plans based on "Restoration Regions" | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system.
14 | Maximum Number of Black Start Units at one site. (Design Comp G) | Currently, only 3 black start units are allowed at one sight without an exception approved by PJM. | Allow more than 3 BS units per site. | [7 empty] | Maintain status quo: max of 3 black start units are allowed at one sight without an exception approved by PJM. |  | Allow more than 3 BS units per site
15 | Cross-Zonal Black Start Addressed (Design Comp H) | TO Based plans but allow BS from other regions/zones. |  |  |  |  | Plans based on "Restoration Regions" | TO Based plans but allow BS from other regions/zones. |  |  | Plans based on "Restoration Regions" | TO Based plans but allow BS from other regions/zones. | Plans remain at TO level except in cases where plans have been aggregated into regions
17 | Units Eligible to be Black Start (Design Component E) | Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource | [8 empty] | Only resources able to start without excitation from BES | Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource
18 | TO's may optionally procure additional BS through bilateral contracts outside PJM OATT (Design Comp F) | TO can optionally acquire additional BS if desired through bilateral contracts (outside of PJM OATT) | [8 empty] | Not permitted | TO can optionally acquire additional BS if desired through bilateral contracts (outside of PJM OATT)
19 | Reactive and Voltage Concerns Addressed (Design Comp H) | Ensure Reactive & Volt / VAR sufficient based on testing and simulations
20 | Cranking Path Issues Addressed (Design Comp H) | Cranking path availability tested during simulations
21 | Fuel Reliability/ Fuel Diversity Addressed (Design Comp G) | Not Considered in Current Restoration Planning | Ensure not too many BS units tie to the same gas pipeline. PJM would consider fuel diversity in selection of BS units | [7 empty] | Require on-site fuel storage | Ensure not too many BS units tie to the same gas pipeline. PJM would consider fuel diversity in selection of BS units
Note on A7: Glen Boyle: Design component removed. M-36 and M-12 being adjusted to remove restoration time target references
Note on A11: Glen Boyle: Design component removed. Compensation issues to be addressed separately.
Note on A14: Glen Boyle: Design component approved. All packages agree
Note on A15: Glen Boyle: Design component approved. All packages agree
Note on A16: Glen Boyle: Design component approved. All packages agree
Note on A17: Glen Boyle: Combined with Design Component 3 (Geography)
Note on A18: Glen Boyle: Design component approved. General agreement between packages.
Note on A20: Glen Boyle: Combined with Design Component 3 (Geography)
Note on A21: Glen Boyle: Design component approved. General agreement between packages.
Note on A22: Glen Boyle: Design component approved. General agreement between packages.
Note on A23: Glen Boyle: Design component approved. General agreement between packages.
Note on A24: Glen Boyle: Design component approved. General agreement between packages.
Note on A25: Glen Boyle: Design component approved. General agreement between packages.
Note on C6: Glen Boyle: Removed package - invalid given the restoration time target removal
Note on D6: Glen Boyle:Removed package - invalid given the restoration time target removal
Note on E6: Glen Boyle: Package removed. Little support based on polling results
Note on F6: Glen Boyle: Package removed. Little support based on polling results
Note on G6: Glen Boyle: Package removed. Little support based on polling results
Note on H6: Glen Boyle: Package removed. Little support based on polling results
Note on K6: Glen Boyle: Package removed. Little support based on polling results
Note on L6: Glen Boyle: Package removed. Little support based on polling results

## Reduced Packages
SRSTF
SOLUTION DETAILS
Instructions: Complete this form as needed. Potential solutions should be populated from the Proposal Matrix
Package Solutions2
|  | Status Quo | Package 1 | Package 1A | Package 2 | Package 2A | Package 2B | Status Quo | Package 2C (High Polling Results) | Package 3 (High Polling Results) | Package 3A | Package 4 | Package 5 (NEW- DUQ) | PJM - IMM Proposal (NEW) | Package 6 (NEW-EXELON)
1 | Restoration Time (Target) | 24 hours |  |  | 48 hours |  | Sliding Restoration Time based on Scenario (72 hours for complete blackout with no outside help) |  | 48 hours | Based on target anywhere from 24-48hrs |  | No time goal; conditions-based restoration
| Coping Power for steam units 4-8 hour start | [6 empty] | TO specific | [5 empty] | Address on case by case basis. Identify units and coping MW required to include in Restoration plan. Supply coping power within required timeframe. May or may not need to committ BS generation to meet these requiremnets | TBD
8 | Amount of black start MW required | Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load + margin on a zonal level | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin) + nuclear safe shutdown power + gas infrastructure load |  | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1, Tier 2 or non-BS) |  |  | Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load + margin on a zonal level | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin + nuclear safe shutdown power + gas infrastructure load | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1 or Tier 2) |  |  |  | (Aux power for all generation that can be restored in four hours + nuclear safe shutdown power + gas infrastructure load) * 110% | (Aux power for all generation that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load) * 110%
2 | Redundancy | Minimum of 3 Units Per Zone ( with Exceptions) |  |  | Minimum one BS unit per Zone |  |  | Minimum of 3 Units Per Zone ( with Exceptions) | 3 BS Units per zone (with exceptions) | 2 BS Units per zone (with exceptions) |  | Minimum of one BS unit per Region | Minimum of one BS unit per Zone regardless of critical load and a Minimum of 2 units per aggrgated zone Explanantion: Each TO should have a black start unit to participate in aggrgate zone black start. The gen could also be used to serve some important loads in cities. Redundancy would be accompished with neighbors' help. | A minimum of 2 black start units assigned to each restoration zone (could be TO zone or aggregated zone (see 'Geography' design component)) that has a critical load requirement | Minimum of 2 BS allocated to each zone with a Critical Load Requirement (with Exceptions)
Z | Restoration Zone (Geography) | TO zone |  | Zones may be aggregated if BS shortages exist | Zones may be aggregated if BS shortages exist |  | Set up Restoration "Regions" for consolidation of restoration plans (i.e. East, West, South, etc) where beneficial | TO zone | TO Zone | TO zone, but allow reactive zonal aggregation based on BS shortages |  |  |  | PJM, in consultation with TOs, to utilize proactive approach in identifying areas of the system where it would be beneficial to aggregate TO zones for restoration purposes (i.e. BS shortages, increased efficiency, availability of BS resources, or increased in speed of restoration); 1) Allow BS from one TO zone to supply critical load in a different TO zone - Redundancy on TO basis - Each TO must have a minimum of 2 BS units (though they may not be physically within TO zone) - Restoration plans at TO level, but coordinated between zones -Selection process opt out option if there is no agreement between PJM / TO 2) Allow critical load and customer load restoration to cross zones - Same BS unit can be used to serve critical load in multiple TO zones - Load pockets in one zone can be served from another zone - Restoration plans at TO level but coordinated between zones - TOs have right of refusal | TO Zone as default with PJM Proactive Review for opportunities for collaboration; TO Based plans but allow BS from other regions/zones with affected TO agreement
12 | Area for Restoration Assumption (Design Comp H) | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  |  |  | Plans based on "Restoration Regions" |  | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  |  |  | Proactive approach to identifying areas of the system where it would be beneficial to aggregate TO Restoration plans; M-36 defining common elements | Entity responsible for BS location
4 | Entity responsible for BS identification | TO; with PJM approval |  | PJM with TO Input | PJM; with TO input | TO, with PJM input | PJM; with TO input | TO, with PJM approval |  |  | PJM with TO input |  |  |  | Shared Responsibility (Status Quo; PJM Dispute Resolution Process used if needed)
5 | Critical Black Start Compensation Outlined | Critical BS (OATT Sched 6A), 13 month test required |  |  | Tier 1: Critical BS (OATT Sched 6A), 13 month test required / Tier 2: Compensation would need to be developed. | [6 empty] | Critical BS (OATT Sched 6A), 13 month test required | Tier 1: Critical BS (OATT Sched 6A), 13 month test required / Tier 2: Compensation would need to be developed. | Critical BS (OATT Sched 6A), 13 month test required | Tiered Approach ?
6 | BS Start Time Requirements | Tier 1 only; 90 minutes close to a dead bus | [5 empty] | Tier 1 only; 90 minutes close to a dead bus | Keep existing Tier 1 BS (90 minute start); Establish Tier 2 BS (same requirements as Tier 1 but a 4 hour start) |  |  |  |  | Start time for BS resources to four hours or less (Nuclear or other critical loadswith specific timing requirements will be prioritized in the selection of black start units) | 90 minutes close to a dead bus
9 | Initial Restoration: Clear Assumption on Outside Assistance (Design Comp C) | Complete PJM blackout with no outside assistance available: working hours.
10 | Initial Restoration: Weather/Load (Design Comp C) | Normal weather pattern, intermediate to peak load, minimal equipment damage and Hot Unit time to start from the Markets database. (Time to start is Notification time + Hot Startup time) | [11 empty] | Normal weather pattern, intermediate to peak load, minimal equipment damage and Hot Unit Start time from the Markets database.
16 | Scenarios in Restoration Drills (Design Comp C) | Plan for worst case, but focus training & analysis on a variety of scenarios
13 | Responsibility for Restoration and coordination (Design Comp H) | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system. | [9 empty] | Plans based on "Restoration Regions" | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system.
14 | Maximum Number of Black Start Units at one site | Currently, only 3 black start units are allowed at one sight without an exception approved by PJM. | [5 empty] | Maximum of 3 per site (with Exceptions) | Allow more than 3 BS units per site.
17 | Units Eligible to be Black Start (Design Component E) | Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource | [9 empty] | Only resources able to start without excitation from BES | Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource
18 | TO's may optionally procure additional BS through bilateral contracts outside PJM OATT (Design Comp F) | TO can optionally acquire additional BS if desired through bilateral contracts (outside of PJM OATT) | [9 empty] | Not permitted | TO can optionally acquire additional BS if desired through bilateral contracts (outside of PJM OATT)
19 | Reactive and Voltage Concerns Addressed (Design Comp H) | Ensure Reactive & Volt / VAR sufficient based on testing and simulations
20 | Cranking Path Issues Addressed (Design Comp H) | Cranking path availability tested during simulations
21 | Fuel Reliability/ Fuel Diversity Addressed (Design Comp G) | Not Considered in Current Restoration Planning | Ensure not too many BS units tie to the same gas pipeline. PJM would consider fuel diversity in selection of BS units | [8 empty] | Require on-site fuel storage | Ensure not too many BS units tie to the same gas pipeline. PJM would consider fuel diversity in selection of BS units
22 | Procurement Option | [6 empty] | RFP | [5 empty] | 5 Year Selection Process with Incremental RFP if needed for interim shortages | TBD
23 | Reliability Backstop? | [6 empty] | No | [5 empty] | Yes, exceptions or TO requirement | TBD

## PJM Package
SRSTF
SOLUTION DETAILS
Instructions: Complete this form as needed. Potential solutions should be populated from the Proposal Matrix
Package Solutions2
|  | Status Quo | Package 1 | Package 1A | Package 2 | Package 2A | Package 2B | Package 2C | Package 3 | Package 3A | Package 4 | Package 5 | PJM - IMM Proposal
1 | Restoration Time (Target) | 24 hours |  |  | 48 hours |  | Sliding Restoration Time based on Scenario (72 hours for complete blackout with no outside help) | 48 hours | Based on target anywhere from 24-48hrs |  | No time goal; conditions-based restoration
2 | Redundancy | Minimum of 3 Units Per Zone ( with Exceptions) |  |  | Minimum one BS unit per Zone |  |  | Minimum of 3 BS units per zone (with Exceptions) | Minimum of 2 BS unit per Zone (with Exceptions) |  | Minimum of one BS unit per Region | Minimum of one BS unit per Zone regardless of critical load and a Minimum of 2 units per aggrgated zone Explanantion: Each TO should have a black start unit to participate in aggrgate zone black start. The gen could also be used to serve some important loads in cities. Redundancy would be accompished with neighbors' help. | Minimum of 2 BS allocated to each zone with a Critical Load Requirement (with Exceptions)
3 | Geography | TO zone |  | Zones may be aggregated if BS shortages exist | Zones may be aggregated if BS shortages exist |  | Set up Restoration "Regions" for consolidation of restoration plans (i.e. East, West, South, etc) where beneficial | TO Zone | Zones may be aggregated if BS shortages exist |  | Set up Restoration "Regions" for consolidation of restoration plans (i.e. East, West, South, etc) where beneficial | Zones may be aggregated if BS shortages exist | Proactive approach to identifying areas of the system where it would be beneficial to aggregate TO Restoration plans
4 | Entity responsible for BS location | TO; with PJM approval |  | PJM with TO Input | PJM; with TO input | TO, with PJM input | PJM; with TO input | TO, with PJM input | TO, with PJM approval | PJM with TO input
5 | Critical Black Start Compensation Outlined | Critical BS (OATT Sched 6A), 13 month test required |  |  | Tier 1: Critical BS (OATT Sched 6A), 13 month test required / Tier 2: Compensation would need to be developed. | [5 empty] | Critical BS (OATT Sched 6A), 13 month test required | Tier 1: Critical BS (OATT Sched 6A), 13 month test required / Tier 2: Compensation would need to be developed. | Critical BS (OATT Sched 6A), 13 month test required
6 | Tiered Approach ? | Tier 1 only; 90 minutes close to a dead bus |  |  | Keep existing Tier 1 BS (90 minute start); Establish Tier 2 BS (same requirements as Tier 1 but a 4 hour start) | [5 empty] | Tier 1 only; 90 minutes close to a dead bus | Keep existing Tier 1 BS (90 minute start); Establish Tier 2 BS (same requirements as Tier 1 but a 4 hour start) | Revise existing requirement of 90 minute start time for BS resources to four hours or less (with exceptions)
8 | Amount of black start MW required | Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load + margin on a zonal level | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin) + nuclear safe shutdown power + gas infrastructure load |  | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1, Tier 2 or non-BS) |  |  | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin + nuclear safe shutdown power + gas infrastructure load | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1 or Tier 2) |  | Based on PJM analysis of available resources (generation, transmission) | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1 or Tier 2) | (Aux power for all generation that can be restored in four hours + nuclear safe shutdown power + gas infrastructure load) * 110%
9 | Initial Restoration: Clear Assumption on Outside Assistance (Design Comp C) | Complete PJM blackout with no outside assistance available: working hours.
10 | Initial Restoration: Weather/Load (Design Comp C) | Normal weather pattern, intermediate to peak load, minimal equipment damage and Hot Unit time to start from the Markets database. (Time to start is Notification time + Hot Startup time) | [10 empty] | Normal weather pattern, intermediate to peak load, minimal equipment damage and Hot Unit Start time from the Markets database.
16 | Scenarios in Restoration Drills (Design Comp C) | Plan for worst case, but focus training & analysis on a variety of scenarios
12 | Area for Restoration Assumption (Design Comp H) | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  |  |  | Plans based on "Restoration Regions" | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  | Plans based on "Restoration Regions" | Plans based on a TO zonal basis with PJM M-36 defining common elements. | Proactive approach to identifying areas of the system where it would be beneficial to aggregate TO Restoration plans; M-36 defining common elements
13 | Responsibility for Restoration and coordination (Design Comp H) | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system. | [8 empty] | Plans based on "Restoration Regions" | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system.
14 | Maximum Number of Black Start Units at one site. (Design Comp G) | Currently, only 3 black start units are allowed at one sight without an exception approved by PJM. | Allow more than 3 BS units per site. | [7 empty] | Maintain status quo: max of 3 black start units are allowed at one sight without an exception approved by PJM. |  | Allow more than 3 BS units per site
15 | Cross-Zonal Black Start Addressed (Design Comp H) | TO Based plans but allow BS from other regions/zones. |  |  |  |  | Plans based on "Restoration Regions" | TO Based plans but allow BS from other regions/zones. |  |  | Plans based on "Restoration Regions" | TO Based plans but allow BS from other regions/zones. | Plans remain at TO level except in cases where plans have been aggregated into regions
17 | Units Eligible to be Black Start (Design Component E) | Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource | [8 empty] | Only resources able to start without excitation from BES | Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource
18 | TO's may optionally procure additional BS through bilateral contracts outside PJM OATT (Design Comp F) | TO can optionally acquire additional BS if desired through bilateral contracts (outside of PJM OATT) | [8 empty] | Not permitted | TO can optionally acquire additional BS if desired through bilateral contracts (outside of PJM OATT)
19 | Reactive and Voltage Concerns Addressed (Design Comp H) | Ensure Reactive & Volt / VAR sufficient based on testing and simulations
20 | Cranking Path Issues Addressed (Design Comp H) | Cranking path availability tested during simulations
21 | Fuel Reliability/ Fuel Diversity Addressed (Design Comp G) | Not Considered in Current Restoration Planning | Ensure not too many BS units tie to the same gas pipeline. PJM would consider fuel diversity in selection of BS units | [7 empty] | Require on-site fuel storage | Ensure not too many BS units tie to the same gas pipeline. PJM would consider fuel diversity in selection of BS units
22 | Procurement Option | [11 empty] | 5 Year Selection Process with Incremental RFP if needed for interim shortages
23 | Reliability Backstop? | [11 empty] | Yes, exceptions or TO requirement
Note on C6: Glen Boyle: Removed package - invalid given the restoration time target removal
Note on D6: Glen Boyle:Removed package - invalid given the restoration time target removal
Note on E6: Glen Boyle: Package removed. Little support based on polling results
Note on F6: Glen Boyle: Package removed. Little support based on polling results
Note on G6: Glen Boyle: Package removed. Little support based on polling results
Note on H6: Glen Boyle: Package removed. Little support based on polling results
Note on K6: Glen Boyle: Package removed. Little support based on polling results
Note on L6: Glen Boyle: Package removed. Little support based on polling results
Note on A7: Glen Boyle: Design component removed. M-36 and M-12 being adjusted to remove restoration time target references
Note on A11: Glen Boyle: Design component removed. Compensation issues to be addressed separately.
Note on A14: Glen Boyle: Design component approved. All packages agree
Note on A15: Glen Boyle: Design component approved. All packages agree
Note on A16: Glen Boyle: Design component approved. All packages agree
Note on A17: Glen Boyle: Combined with Design Component 3 (Geography)
Note on A18: Glen Boyle: Design component approved. General agreement between packages.
Note on A20: Glen Boyle: Combined with Design Component 3 (Geography)
Note on A21: Glen Boyle: Design component approved. General agreement between packages.
Note on A22: Glen Boyle: Design component approved. General agreement between packages.
Note on A23: Glen Boyle: Design component approved. General agreement between packages.
Note on A24: Glen Boyle: Design component approved. General agreement between packages.
Note on A25: Glen Boyle: Design component approved. General agreement between packages.

## Packages for Voting
|  | Status Quo | Package 1 | Package 1A | Package 2 | Package 2A | Package 2B | Status Quo | Package 2C (High Polling Results) | Package 3 (High Polling Results) | Package 3A | Package 4 | Package 5 (NEW- DUQ) | PJM - IMM Proposal (NEW) | Package 6 (NEW-EXELON)
1 | Restoration Time (Target) | 24 hours |  |  | 48 hours |  | Sliding Restoration Time based on Scenario (72 hours for complete blackout with no outside help) |  | 48 hours | Based on target anywhere from 24-48hrs |  | No time goal; conditions-based restoration
2 | Amount of black start MW required | Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load + margin on a zonal level | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin) + nuclear safe shutdown power + gas infrastructure load |  | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1, Tier 2 or non-BS) |  |  | Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load + margin on a zonal level | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin + nuclear safe shutdown power + gas infrastructure load | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1 or Tier 2) |  |  |  | (Aux power for all generation that can be restored in four hours + nuclear safe shutdown power + gas infrastructure load) * 110% | (Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load) * 110%
3 (ADDED) | Coping Power for units 4-8 hour start | TO Specific | [5 empty] | TO specific | [5 empty] | Address on case by case basis. Identify units and coping MW required to include in Restoration plan. Supply coping power within required timeframe. May or may not need to committ BS generation to meet these requiremnets | N/A
4 | Redundancy | Minimum of 3 black start units per TO zone ( with Exceptions) |  |  | Minimum one BS unit per Zone |  |  | Minimum of 3 Units Per Zone ( with Exceptions) | 3 BS Units per zone (with exceptions) | 2 BS Units per zone (with exceptions) |  | Minimum of one BS unit per Region | Minimum of one BS unit per Zone regardless of critical load and a Minimum of 2 units per aggrgated zone Explanantion: Each TO should have a black start unit to participate in aggrgate zone black start. The gen could also be used to serve some important loads in cities. Redundancy would be accompished with neighbors' help. | A minimum of 2 black start units assigned to each restoration zone that has a critical load requirement (restoration zone could be TO zone or aggregated zone (see Cross Zonal Coordination' Level 1, 2, and 3 & 'Restoration Zone (Geography)' design components below)) | Minimum of 2 BS allocated to each zone with a Critical Load Requirement (with Exceptions)
5 | Maximum Number of Black Start Units at one site | Currently, only 3 black start units are allowed at one sight without an exception approved by PJM. | [5 empty] | Maximum of 3 per site (with Exceptions) | Allow more than 3 BS units per site.
6 | Restoration Zone (Geography) | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  | Zones may be aggregated if BS shortages exist | Zones may be aggregated if BS shortages exist |  | Set up Restoration "Regions" for consolidation of restoration plans (i.e. East, West, South, etc) where beneficial | TO zone | TO Zone | TO zone, but allow reactive zonal aggregation based on BS shortages |  |  |  | PJM, in consultation with TOs, to use proactive approach in identifying areas of the system where it would be beneficial to employ cross TO zonal coordination for restoration purposes (i.e. BS shortages, increased efficiency, availability of BS resources, or increased in speed of restoration). See 'Cross Zonal Coordination' level 1, 2, and 3 design components below) | TO Zone as default with PJM Proactive Review for opportunities for collaboration; TO Based plans but allow BS from other regions/zones with affected TO agreement
12 | Area for Restoration Assumption (Design Comp H) | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  |  |  | Plans based on "Restoration Regions" |  | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  |  |  | Proactive approach to identifying areas of the system where it would be beneficial to aggregate TO Restoration plans; M-36 defining common elements (See Cross-Zonal Coordination design components) | Entity responsible for BS location
7 (ADDED) | Cross Zonal Coordination (Level 1) - Allow BS from outside TO zone to meet TO critical load | Case by case - only in response to RFP if shortages | [11 empty] | In collaboration with TO, PJM may select BS outside of a TO zone to serve critical load within that zone based on opportunities to: - eliminate BS shortages in zone (reliability requirement) - meet critical load restoration timing requirements (reliability requirement) - improve restoration speed or efficiency (efficiency opportunity) - significantly reduce cost (efficiency opportunity) TO zones stay in place as the restoration zone. Redundancy on TO zone basis (i.e. 2 BS units allocated to each TO zone; though physically may be outside zone) Restoration Plans remain on TO level, but coordinated between TOs. If TO disagrees with BS unit selection, they may "opt out" of selection and acquire their own BS outside of OATT (see 'Opt out' design component below) | See row 6.
8 (ADDED) | Cross Zonal Coordination (Level 2) - Allow critical load and customer load to be restored across TO zones | Cranking power may be supplied across zones | [11 empty] | In collaboration with TO, PJM will look for opportunities to serve critical load or customer load pockets in one TO zone from generation (BS or otherwise) in a nearby TO zone based on opportunities to: - eliminate BS shortages in zone (reliability requirement) - meet critical load restoration timing requirements (reliability requirement) - improve restoration speed or efficiency (efficiency opportunity) - significantly reduce cost (efficiency opportunity) Same BS unit may be used to serve critical load in more than one nearby TO zone. TO zones stay in place as the restoration zone. Redundancy on TO zone basis (i.e. 2 BS units allocated to each zone; though physically may be outside zone) Restoration Plans remain at TO level, but are coordinated between involved TOs. Cross zonal coordination may be required by PJM to meet reliability requirements. If TO does not agree, TO may opt out (as defined by the 'Opt Out' Design component below) If cross zonal coordination is suggested to increase efficiency (improve restoration speed or reduce cost,) TO may refuse coordination opportunity. | See row 6.
9 (ADDED) | Cross Zonal Coordination (LEVEL 3) - Full Aggregation of TO zones for Restoration | Not done | [11 empty] | In collaboration with TO, PJM will look for opportunities to fully aggregate TO zones for restoration purposes based on opportunities to: - eliminate BS shortages in zone (reliability requirement) - meet critical load restoration timing requirements (reliability requirement) - improve restoration speed or efficiency (efficiency opportunity) - significantly reduce cost (efficiency opportunity) This could be in the form of merging TO restoration zones and associated restoration plans or creating new Restoration regions (new boundaries) and a new restoration plan for the new restoration region. Redundancy requirements would be on a Restoration Region basis (i.e minimum of 2 BS units for the new Restoration region). Any affected TO and PJM would have to agree to this aggregation. If there is not agreement, the aggration will not occur ('opt out' option not needed, just refusal) | See row 6.
10 | Entity responsible for BS identification | TO; with PJM approval |  | PJM with TO Input | PJM; with TO input | TO, with PJM input | PJM; with TO input | TO, with PJM approval |  |  | PJM with TO input (PJM as the TOP has ultimate responsibility though will look to collaborate and coordinate with the TO in the development of the plan including the amount and placement of BS) TO has "opt out" provision to acquire BS outside PJM OATT. TO has Dispute Resolution Process if disagreement. |  |  |  | Shared Responsibility (Status Quo; PJM Dispute Resolution Process used if needed)
11 | Entity responsibile for executing the restoration plans and overall coordination | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system. | [11 empty] | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system.
12 | BS Start Time Requirements | 90 minutes close to a dead bus | [5 empty] | Tier 1 only; 90 minutes close to a dead bus | Keep existing Tier 1 BS (90 minute start); Establish Tier 2 BS (same requirements as Tier 1 but a 4 hour start) |  |  |  |  | Start time for BS resources to four hours or less (Nuclear or other critical loads with specific timing requirements will be prioritized in the selection of black start units) | Status Quo
13 | Initial Restoration: Clear Assumption on Outside Assistance | Complete PJM blackout with no outside assistance available: working hours.
14 | Initial Restoration: Weather/Load | Normal weather pattern, intermediate to peak load, minimal equipment damage and Hot Unit time to start from the Markets database. (Time to start is Notification time + Hot Startup time)
15 | Scenarios in Restoration Drills | Plan for worst case, but focus training & analysis on a variety of scenarios
16 | Units Eligible to be Black Start | Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource
17 | TO's may optionally procure additional BS through bilateral contracts outside PJM OATT | TO can optionally acquire additional or different BS if desired through bilateral contracts (outside of PJM OATT)
18 (Added) | Opt Out | TO can acquire BS through bilateral contracts outside of PJM OATT. | [11 empty] | If TO does not agree with PJM's selection of BS units, inclusive of level of cross-zonal coordination, TO can opt out of the RFP for Black Start and acquire additional or different BS through bilateral contracts. This will occur outside of PJM OATT. Costs will not be collected or distributed through PJM's Tariff. TO will need to provide PJM evidence that the BS selected by the TO can meet PJM's BS requirements. | Status Quo
19 | Reactive and Voltage Concerns Addressed | Ensure Reactive & Volt / VAR sufficient based on testing and simulations
20 | Cranking Path Issues Addressed | Cranking path availability tested during simulations
21 | Fuel Reliability/ Fuel Diversity Addressed | Not Considered in Current Restoration Planning | Ensure not too many BS units tie to the same gas pipeline. PJM would consider fuel diversity in selection of BS units | [8 empty] | Require on-site fuel storage | Ensure not too many BS units dependent on same gas pipeline. PJM would consider fuel diversity in selection of BS units
22 | Black Start Compensation | OATT Sched 6A, 13 month test required | [11 empty] | OATT Sched 6A, 13 month test required (to be discussed further in the System Restoration Strategy TF) | Deferred (to be discussed further in Q1 2013 in the System Restoration Strategy TF)
23 | Procurement Option | RFP | [5 empty] | RFP | [5 empty] | 5 Year Selection Process with Incremental RFP if needed for interim shortages | 5 year Selection Process with Incremental RFP if needed for interim shortages (incorporating the other design components above)
24 | Reliability Backstop? | Exceptions to reliability criteria | [5 empty] | No | [5 empty] | Detailed exception process and other options | Detailed exception process and other options (incorporating the other design components above)

## Matrix including COST Allocatio
|  | Status Quo | Package 1 | Package 1A | Package 2 | Package 2A | Package 2B | Status Quo | Package 2C (High Polling Results) | Package 3 (High Polling Results) | Package 3A | Package 4 | Package 5 (NEW- DUQ) | PJM - IMM Proposal (NEW) | Package 6 (NEW-EXELON)
1 | Restoration Time (Target) | 24 hours |  |  | 48 hours |  | Sliding Restoration Time based on Scenario (72 hours for complete blackout with no outside help) |  | 48 hours | Based on target anywhere from 24-48hrs |  | No time goal; conditions-based restoration
2 | Amount of black start MW required | Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load + margin on a zonal level | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin) + nuclear safe shutdown power + gas infrastructure load |  | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1, Tier 2 or non-BS) |  |  | Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load + margin on a zonal level | Stage 1 critical load (critical aux power for units that can be restored in 8 hours + % margin + nuclear safe shutdown power + gas infrastructure load | Stage 1 critical load (critical aux power for units that can be started in 8 hours + % margin); Stage 2 critical load (nuclear safe shutdown and gas infrastructure) would be targeted to be restored in 4 hours (could be met with Tier 1 or Tier 2) |  |  |  | (Aux power for all generation that can be restored in four hours + nuclear safe shutdown power + gas infrastructure load) * 110% | (Aux power for critical steam that can be restored in 8 hours + nuclear safe shutdown power + gas infrastructure load) * 110%
3 (ADDED) | Coping Power for units 4-8 hour start | TO Specific | [5 empty] | TO specific | [5 empty] | Address on case by case basis. Identify units and coping MW required to include in Restoration plan. Supply coping power within required timeframe. May or may not need to committ BS generation to meet these requiremnets | N/A
4 | Redundancy | Minimum of 3 black start units per TO zone ( with Exceptions) |  |  | Minimum one BS unit per Zone |  |  | Minimum of 3 Units Per Zone ( with Exceptions) | 3 BS Units per zone (with exceptions) | 2 BS Units per zone (with exceptions) |  | Minimum of one BS unit per Region | Minimum of one BS unit per Zone regardless of critical load and a Minimum of 2 units per aggrgated zone Explanantion: Each TO should have a black start unit to participate in aggrgate zone black start. The gen could also be used to serve some important loads in cities. Redundancy would be accompished with neighbors' help. | A minimum of 2 black start units assigned to each restoration zone that has a critical load requirement (restoration zone could be TO zone or aggregated zone (see Cross Zonal Coordination' Level 1, 2, and 3 & 'Restoration Zone (Geography)' design components below)) | Minimum of 2 BS allocated to each zone with a Critical Load Requirement (with Exceptions)
5 | Maximum Number of Black Start Units at one site | Currently, only 3 black start units are allowed at one sight without an exception approved by PJM. | [5 empty] | Maximum of 3 per site (with Exceptions) | Allow more than 3 BS units per site.
6 | Restoration Zone (Geography) | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  | Zones may be aggregated if BS shortages exist | Zones may be aggregated if BS shortages exist |  | Set up Restoration "Regions" for consolidation of restoration plans (i.e. East, West, South, etc) where beneficial | TO zone | TO Zone | TO zone, but allow reactive zonal aggregation based on BS shortages |  |  |  | PJM, in consultation with TOs, to use proactive approach in identifying areas of the system where it would be beneficial to employ cross TO zonal coordination for restoration purposes (i.e. BS shortages, increased efficiency, availability of BS resources, or increased in speed of restoration). See 'Cross Zonal Coordination' level 1, 2, and 3 design components below) | TO Zone as default with PJM Proactive Review for opportunities for collaboration; TO Based plans but allow BS from other regions/zones with affected TO agreement
12 | Area for Restoration Assumption (Design Comp H) | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  |  |  | Plans based on "Restoration Regions" |  | Plans based on a TO zonal basis with PJM M-36 defining common elements. |  |  |  |  | Proactive approach to identifying areas of the system where it would be beneficial to aggregate TO Restoration plans; M-36 defining common elements (See Cross-Zonal Coordination design components) | Entity responsible for BS location
7 (ADDED) | Cross Zonal Coordination (Level 1) - Allow BS from outside TO zone to meet TO critical load | Case by case - only in response to RFP if shortages | [11 empty] | In collaboration with TO, PJM may select BS outside of a TO zone to serve critical load within that zone based on opportunities to: - eliminate BS shortages in zone (reliability requirement) - meet critical load restoration timing requirements (reliability requirement) - improve restoration speed or efficiency (efficiency opportunity) - significantly reduce cost (efficiency opportunity) TO zones stay in place as the restoration zone. Redundancy on TO zone basis (i.e. 2 BS units allocated to each TO zone; though physically may be outside zone) Restoration Plans remain on TO level, but coordinated between TOs. If TO disagrees with BS unit selection, they may "opt out" of selection and acquire their own BS outside of OATT (see 'Opt out' design component below) | See row 6.
8 (ADDED) | Cross Zonal Coordination (Level 2) - Allow critical load and customer load to be restored across TO zones | Cranking power may be supplied across zones | [11 empty] | In collaboration with TO, PJM will look for opportunities to serve critical load or customer load pockets in one TO zone from generation (BS or otherwise) in a nearby TO zone based on opportunities to: - eliminate BS shortages in zone (reliability requirement) - meet critical load restoration timing requirements (reliability requirement) - improve restoration speed or efficiency (efficiency opportunity) - significantly reduce cost (efficiency opportunity) Same BS unit may be used to serve critical load in more than one nearby TO zone. TO zones stay in place as the restoration zone. Redundancy on TO zone basis (i.e. 2 BS units allocated to each zone; though physically may be outside zone) Restoration Plans remain at TO level, but are coordinated between involved TOs. Cross zonal coordination may be required by PJM to meet reliability requirements. If TO does not agree, TO may opt out (as defined by the 'Opt Out' Design component below) If cross zonal coordination is suggested to increase efficiency (improve restoration speed or reduce cost,) TO may refuse coordination opportunity. | See row 6.
9 (ADDED) | Cross Zonal Coordination (LEVEL 3) - Full Aggregation of TO zones for Restoration | Not done | [11 empty] | In collaboration with TO, PJM will look for opportunities to fully aggregate TO zones for restoration purposes based on opportunities to: - eliminate BS shortages in zone (reliability requirement) - meet critical load restoration timing requirements (reliability requirement) - improve restoration speed or efficiency (efficiency opportunity) - significantly reduce cost (efficiency opportunity) This could be in the form of merging TO restoration zones and associated restoration plans or creating new Restoration regions (new boundaries) and a new restoration plan for the new restoration region. Redundancy requirements would be on a Restoration Region basis (i.e minimum of 2 BS units for the new Restoration region). Any affected TO and PJM would have to agree to this aggregation. If there is not agreement, the aggration will not occur ('opt out' option not needed, just refusal) | See row 6.
10 | Entity responsible for BS identification | TO; with PJM approval |  | PJM with TO Input | PJM; with TO input | TO, with PJM input | PJM; with TO input | TO, with PJM approval |  |  | PJM with TO input (PJM as the TOP has ultimate responsibility though will look to collaborate and coordinate with the TO in the development of the plan including the amount and placement of BS) TO has "opt out" provision to acquire BS outside PJM OATT. TO has Dispute Resolution Process if disagreement. |  |  |  | Shared Responsibility (Status Quo; PJM Dispute Resolution Process used if needed)
11 | Entity responsibile for executing the restoration plans and overall coordination | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system. | [11 empty] | Restoration performed at TO zonal level with PJM coordination of interconnection of areas and EHV system.
12 | BS Start Time Requirements | 90 minutes close to a dead bus | [5 empty] | Tier 1 only; 90 minutes close to a dead bus | Keep existing Tier 1 BS (90 minute start); Establish Tier 2 BS (same requirements as Tier 1 but a 4 hour start) |  |  |  |  | Start time for BS resources to four hours or less (Nuclear or other critical loads with specific timing requirements will be prioritized in the selection of black start units) | Status Quo
13 | Initial Restoration: Clear Assumption on Outside Assistance | Complete PJM blackout with no outside assistance available: working hours.
14 | Initial Restoration: Weather/Load | Normal weather pattern, intermediate to peak load, minimal equipment damage and Hot Unit time to start from the Markets database. (Time to start is Notification time + Hot Startup time)
15 | Scenarios in Restoration Drills | Plan for worst case, but focus training & analysis on a variety of scenarios
16 | Units Eligible to be Black Start | Any resource capable of meeting minimum requirements should be eligible to be considered as a BS resource
17 | TO's may optionally procure additional BS through bilateral contracts outside PJM OATT | TO can optionally acquire additional or different BS if desired through bilateral contracts (outside of PJM OATT)
18 (Added) | Opt Out | TO can acquire BS through bilateral contracts outside of PJM OATT. | [11 empty] | If TO does not agree with PJM's selection of BS units, inclusive of level of cross-zonal coordination, TO can opt out of the RFP for Black Start and acquire additional or different BS through bilateral contracts. This will occur outside of PJM OATT. Costs will not be collected or distributed through PJM's Tariff. TO will need to provide PJM evidence that the BS selected by the TO can meet PJM's BS requirements. | Status Quo
19 | Reactive and Voltage Concerns Addressed | Ensure Reactive & Volt / VAR sufficient based on testing and simulations
20 | Cranking Path Issues Addressed | Cranking path availability tested during simulations
21 | Fuel Reliability/ Fuel Diversity Addressed | Not Considered in Current Restoration Planning | Ensure not too many BS units tie to the same gas pipeline. PJM would consider fuel diversity in selection of BS units | [8 empty] | Require on-site fuel storage | Ensure not too many BS units dependent on same gas pipeline. PJM would consider fuel diversity in selection of BS units
22 | Black Start Compensation | OATT Sched 6A, 13 month test required | [11 empty] | OATT Sched 6A, 13 month test required (to be discussed further in the System Restoration Strategy TF) | Deferred (to be discussed further in Q1 2013 in the System Restoration Strategy TF)
23 | Procurement Option | RFP | [5 empty] | RFP | [5 empty] | 5 Year Selection Process with Incremental RFP if needed for interim shortages | 5 year Selection Process with Incremental RFP if needed for interim shortages (incorporating the other design components above)
24 | Reliability Backstop? | Exceptions to reliability criteria | [5 empty] | No | [5 empty] | Detailed exception process and other options | Detailed exception process and other options (incorporating the other design components above)
25 | Cost Allocation | [14 empty] | Other Options?
25a | Cross Zonal Level 1 - Nominated BS Unit in External TO Zone | PJM Tariff allows BS Unit Annual Revenues (regardless of zonal location) to be allocated to nominating zone. | [11 empty] | Develop Annual Revenue Requirement for External TO (TO where BS is located) for NERC-CIP and other capital cost recovery in Schedule 6A.
Use existing Capital Recovery Factors for external TO capital costs with 5 year recovery period.
External TO recovers actual O&M costs for Cross Zonal Coordination
External TO recovers same Training Cost as Generator
Use existing Generator Cost Approval Process in Schedule 6A (IMM reviews and approves all costs).
External TO Incentive Factor equal to zero.
25b | Cross Zonal Level 2 - BS Unit Shared by more than one TO Zones | PJM Tariff allows BS Unit Annual Revenues (regardless of zonal location) to be allocated to nominating zone. | [11 empty] | Allocate Unit Annual BS revenues to each zone by critical load percentage
25c | Cross Zonal Level 3 - Partial or Complete Aggregation of TO Zones for BS | PJM Tariff allows BS Unit Annual Revenues (regardless of zonal location) to be allocated to nominating zone. | [11 empty] | Full aggregation of TO Zone: Allocate aggregated TO Zones units' annual BS revenues to each zone by critical load percentage Partial aggregation of zones: Allocate aggregated region units' annual BS revenues to respective TO by critical load percentage