## PublicVersion
Need Number | TO | Area | Needs Meeting | Solutions Meeting | Integration of Supplemental Projects for Inclusion in Local Plan | Upgrade ID | Withdrawn | Facility | Project Description
ACE-2018-0004 | ACE | PJM MA | 2018-10-29 | 2019-01-25 |  | S2099 |  | Deterioration on Mickleton - Paulsboro - Valero 69 kV line. | Inspection revealed deterioration on Mickleton - Paulsboro - Valero 69 kV line.
ACE-2018-0005 | ACE | PJM MA | 2018-10-29 | Cancel |  |  |  | Deteriorated equipment at 138/12 kV Scull Substation | Inspections revealed deteriorated equipment at 138/12 kV Scull Substation
AEP-2018-AP009 | AEP | PJM West | 2018-11-29 |  |  |  |  | Babcock & Wilcox Upgrade Request. | Babcock & Wilcox (B&W) requested to upgrade their existing 12 kV service to 69 kV and be served directly from the B&W 69 kV bus. Expected peak demand is approximately 16 MVA.
AEP-2018-AP010 | AEP | PJM West | 2018-11-29 | 2020-01-17 | 2020-04-20 | S2200 |  | Paintsville, KY | From 2013-2018 the Falcon -Prestonsburg 46 kV circuit (~ 23 miles) has experienced 19 momentary and permanent outages. Over the last three years the circuit has experienced 1.77 million customer minutes of interruption. The ~14.5 mile 46 kV line section between Falcon and Middle Creek has 84 category A open conditions associated with the structures that make up the line. These conditions include damaged/rotted poles and damaged guy wires, cross arms. The majority of this line utilizes 1950s wood structures and 3/0 ACSR conductor. The ~8.5 mile 46 kV line section between Middle Creek and Prestonsburg has 27 category A open conditions associated with the structures that make up the line. These conditions include damaged/rotted poles and damaged guy wires, cross arms. About half the structures that make up the line are 1940s wood structures with the majority of the line utilizing 1/0 Cu. conductor.
AEP-2018-AP011 | AEP | PJM West | 2018-11-29 | 2020-06-19 | 2020-09-15 | s2281 |  | Capacitor switchs at Inez station | Capacitor switchers ‘BB’ and ‘CC’ at Inez station are Mark V model which no longer support modern relaying packages. Mark V’s have been historically prone to mechanism failures and are being replaced system wide where possible. S&C circuit switcher ‘AA’ at Inez station is an S&C 2030 type with no gas monitor. The Inez 138 kV yard was designed as a breaker and a half station, but the ‘B’ string was never completed leaving dissimilar zones of protection between the #1 bus and 20+ mile Inez to Johns Creek 138 kV circuit. Dissimilar zones of protection also exist between the 138 kV bus #2, 138/69 kV transformer #1, and the 138 kV circuit to the Martiki coal service point.
AEP-2018-AP013 | AEP | PJM West | 2019-01-11 | 2019-12-18 | 2020-01-29 | S2166 |  | Lakin - Racine 69 kV circuit condition | The Lakin - Racine 69 kV circuit (~13.2 mi) currently has 125 open conditions on 63/91 structures. These conditions include rot top, woodpecker damage, burnt insulator, broken knee/V braces. The majority of the circuit is constructed with 1960s wood structures. From 2015-2018, the line has experienced 8 momentary and 3 permanent outages which have resulted in 27k customer minutes of interruption. The 69kV CB F at Lakin is a CF type oil filled breaker. Oil filled breakers have significant maintenance requirements due to oil handling. This CB model family has experienced numerous documented mechanism bearing issues and failures within the AEP population. Lakin Substation deploys 42 relays implemented to ensure the adequate protection and operation of the substation. Currently 35 of the 42 relays (83% of all station relays) are in need of replacement. There are 32 electromechanical, 2 legacy ABB DPU microprocessor, and 1 static type relays with significant limitations in regards to spare part availability in addition to a lack of vendor support. The electromechanical and static relays have no capability for fault data collection and retention. The ABB DPU relays pose a safety risk to persons performing breaker operation because the DPUs are mounted directly on the circuit breaker without a delay for opening and closing the breaker. If there is any arcing or something goes wrong as the breaker operates, the operator is now in the line of fire.Ã‚Â Modern relays can program a delay (10 seconds) after an open or close button is pressed so the operator can have time to walk out of the line of fire. The 138kV line switches are mounted on cap and pin insulators at Lakin. The current MOAB/Ground SW configurations at Lakin create faults in the station to signal the remote end breakers to open; this results in Transmission lines breakers getting burdened to clear Transformer faults thus reducing their life span. Lakin 138/69 kV transformer bank #1 CO and CO2 levels have been on the rise since 2004 when all transformer bushings were replaced during minor transformer maintenance activities; the oil was processed at that time, accounting for the rapid decrease in gas concentrations in 2004. The latest CO reading of 493ppm is significantly high. Moisture content had been trending up from 2008 to 2016 and has been in excess of 25ppm since 2016. Dielectric strength is currently trending up, but this rapid and significant 15.1kV increase was unexpected given the minor drop in moisture content levels from 2016 to 2017. Together, these are potential indicators of insulating paper breakdown. In addition, H2 concentrations have been rising since 2004. The presence of H2 indicates the potential for stray gassing in the oil and carbonization of the insulating paper. The above conditions indicate a strong probability of degradation of the integrity of the paper insulation surrounding the transformer windings from carbonization, breakdown in cellulose, or both.
AEP-2018-AP016 | AEP | PJM West | 2019-01-11 | 2020-01-17 | 2020-01-29 | S2179 |  | Wythe 138/69 kV transformer | Wythe 138/69 kV transformer has experienced thermal through fault events, mostly in excess of 700 C, have led to numerous overheating events, steady increases in gasses including high levels of ethylene and ethane, and carbonization of the insulating paper. The oil's interfacial tension is showing signs of sludge beginning to form due to the carbonization created contaminants. In addition, the moisture content is beginning to climb which has not yet been reflected in a drop in dielectric strength. Wythe circuit breaker F is an FK type oil filled breaker. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. The FK-439-115-3500-3 is no longer vendor supported and is 1 of 2 remaining on the AEP system, making spare parts difficult or impossible to acquire. Wythe circuit breaker M is a CF type oil filled breaker. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. This particular unit has a recorded malfunction related to a broken S.S. line on the maintenance valve and pressure switches. Byllesby circuit breakers B and D are oil filled breakers manufactured in 1952 and 1965 respectively. Both breakers have exceeded the designed number of fault operations (10). These breakers are GE FK type oil breakers with no oil containment. The GE FK type breakers are known to have an internal operating mechanism that are prone to high failure rates. Galax circuit breakers G, F, and H are all GE FK type oil breakers with no oil containment. The GE FK type breakers are known to have an internal operating mechanism that are prone to high failure rates. Circuit Breakers G, F, and H are all approximately 50 years old and have exceeded the designed number of fault operations (10). Jubal Early 138/69kV Transformer has reoccurring bushing damage, dielectric strength breakdown (insulation breakdown) and short circuit breakdown (due to fault events). Recent test reports show oil interfacial tension to be below the minimum acceptable level for a unit of this voltage class. Reduction in oil interfacial tension is related to oil contamination and presence of oxidation byproducts in the oil. Huffman - Willis Gap 138 kV is a 15 mile long radial line that serves approximately 25 MVA of load at Willis Gap 138 kV station. There is approximately a total of 230 MVA of load being served on the 138 kV and 69 kV networks throughout Carroll County, Wythe County, Grayson County and Galax City. Approximately 120 MVA is served off of the 138 kV line from Jacksons Ferry - Huffman - Wythe. The 69 kV network around Cliffview/Galax/Fries serves approximately 110 MVA. Under N-1-1 scenarios involving the 138 kV sources there is the potential to drop all 230 MVA of load. Originally, AEP proposed supplemental project S1295 to address this concern. Based on recent needs identified in Floyd County VA, AEP believes a more holistic solution exists to resolve these needs collectively. AEP has recommended cancelation of supplemental project S1295 (Presented 5/31/2017 SRTEAC).
AEP-2018-AP017 | AEP | PJM West | 2019-01-11 |  |  |  |  | 138 kV breakers at West Kingsport station | 138 kV circuit breaker "E" at West Kingsport station is a type FX-11 breaker, which is one of only two remaining circuit breakers of this class on the AEP system . Due to a lack of spare replacement parts, it is not possible to maintain the breaker in the event of a failure. Breaker "E" has had historical issues with gas leaks. In addition, this circuit breaker has experienced 30 fault operations exceeding the manufacturers recommendation 10. Currently dissimilar zones of protection exist at the West Kingsport between the 138 kV bus #1, 138 kV circuit towards North Bristol (~25 miles), and the 138 kV service point towards the Royal Ordnance Ammunitions Plant. The existing configuration at West Kingsport station results in an outage of the entire 138 kV yard and all customers served from the station for a failure of 138 kV circuit breaker "G".
AEP-2018-AP017 | AEP | PJM West | 2019-01-11 | 2020-12-18 |  |  |  | 138 kV breakers at West Kingsport station | 138 kV circuit breaker "E" at West Kingsport station is a type FX-11 breaker, which is one of only two remaining circuit breakers of this class on the AEP system . Due to a lack of spare replacement parts, it is not possible to maintain the breaker in the event of a failure. Breaker "E" has had historical issues with gas leaks. In addition, this circuit breaker has experienced 30 fault operations exceeding the manufacturers recommendation 10. Currently dissimilar zones of protection exist at the West Kingsport between the 138 kV bus #1, 138 kV circuit towards North Bristol (~25 miles), and the 138 kV service point towards the Royal Ordnance Ammunitions Plant. The existing configuration at West Kingsport station results in an outage of the entire 138 kV yard and all customers served from the station for a failure of 138 kV circuit breaker "G".
AEP-2018-AP018 | AEP | PJM West | 2019-01-11 | 2020-07-17 | 2020-10-21 | s2348 |  | Chemical Area Project | Chemical 138/46 kV XF #1 has been declared a failure. Operations has noted that Chemical 138/46 kV XF #1 fans and cooling system are not working properly and winding temperature was documented at an extremely hot level of 109 C prior to taking the unit offline in 2017.Ã‚Â There are no parts attainable to repair the obsolete cooling system. In addition, interfacial tension has been diminished since 2002. This is an early indication of the development of sludge which can impede oil circulation, further hampering the ability of the unit to cool. Based on dissolved gas analysis, the observed gas concentrations, specifically of ethylene and acetylene, are likely the result of a mixture of thermal and electrical faults along with the carbonization of the insulating paper. The signal of insulation paper carbonization, which generates particles in the oil, highly correlates to the generation of sludge indicated by the interfacial tension. Chemical 138/46 kV XF #2 moisture levels have recently been increasing, resulting in downward trending dielectric strength. In addition, interfacial tension has been on the decline. This is an early indication of the development of sludge which can impede oil circulation and cooling. Operations has noted numerous conditions with this unit, most critical of which is that the bank was derated to 33.75MVA because only one pump of three is operational for the cooling system. There are no parts attainable to repair the obsolete cooling system. The 46kV CBs C, G, H, Q, R, and S are oil filled breakers without secondary oil containment. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 equivalents do not require. CBs G and H are 2 of 40 in the FK-72.5-27000-10 model family remaining on the AEP system. CB A is the last FK-339-46-1500-Y model on the entire AEP system. CBs B, Q, R, and S are the last 4 in the FK-339-46-1500-5 model family remaining on the entire AEP system. CB C is the last FK-46-1500 model on the entire AEP system. This scarcity of sister units makes finding spare parts for these units difficult to impossible, and these models are no longer vendor supported. The 46kV CS CC is an S&C 2030-69 model. The S&C 2030 circuit switcher model family has no gas monitor and sister units on the AEP System have experienced malfunctions; the major ones include gas loss, interrupter failures, and operating mechanism failures.
AEP-2018-AP019 | AEP | PJM West | 2019-01-11 | 2019-12-18 | 2020-01-29 | S2165 |  | Nitro 69 kV circuit breakers | Nitro 69 kV circuit breakers G and H are CF-48 oil type breakers that were manufactured in the 1960s. In general, oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance, which could cause environmental and safety hazards. In addition, breakers G and H have experienced 42 and 39 faults of operation, respectively. These both exceed the manufacturers designed number of fault operations of 10. "
AEP-2018-AP021 | AEP | PJM West | 2018-11-29 |  |  |  |  | Baltimore/Lancaster, Ohio | Baltimore 69kV CBs E and F are oil type breakers (vintage 1951) and have been identified for replacement due to lack of spare part availability, historical reliability, and lack of vendor support. Oil breakers are difficult to maintain due to oil handling requirements. Oil spills can occur during maintenance and fixes. The breakers have experienced the following fault operations: CB E (5), CB F (5). Baltimore currently has 20 electro-mechanical relays employed. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. Lancaster 69kV CBs B and D are oil type breakers (vintage 1989) and have been identified for replacement due to lack of spare part availability, historical reliability, and lack of vendor support. Oil breakers are difficult to maintain due to oil handling requirements. Oil spills can occur during maintenance and fixes. The breakers have experienced the following fault operations: CB B (4), CB D (18). Lancaster currently has 46 electro-mechanical relays employed. EM relays have limited vendor support, lack SCADA functionality, and don’t offer fault data collection.
AEP-2018-AP022 | AEP | PJM West | 2018-11-29 |  |  |  |  | Coshocton, Ohio | Cyclops 69kV circuit switcher A is currently being used as a line CB. This model has limited spare parts availability and reliability concerns. This circuit switcher has also experienced 41 fault operations. Cyclops 69kV CB B is an oil type breaker (vintage 1955) that has exceeded the manufacturers recommended number of fault operations (36 total faults). Oil breakers are difficult to maintain due to oil handling requirements. Oil spill can occur during maintenance and fixes. Cyclops station currently has 19 electro-mechanical relays employed. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. Cyclops station is currently built upon a four-pole wooden bay that is progressively deteriorating.
AEP-2018-AP022 | AEP | PJM West | 2018-11-29 |  |  |  |  | Coshocton, Ohio | Cyclops 69kV circuit switcher A is currently being used as a line CB. This model has limited spare parts availability and reliability concerns. This circuit switcher has also experienced 41 fault operations. Cyclops 69kV CB B is an oil type breaker (vintage 1955) that has exceeded the manufacturers recommended number of fault operations (36 total faults). Oil breakers are difficult to maintain due to oil handling requirements. Oil spill can occur during maintenance and fixes. Cyclops station currently has 19 electro-mechanical relays employed. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. Cyclops station is currently built upon a four-pole wooden bay that is progressively deteriorating.
AEP-2018-AP020 | AEP | PJM West | 2019-01-11 | 2020-01-17 | 2020-01-29 | S2179 |  | Condition of Claytor - West Bassett 138 kV circuit | The Clayton - West Bassett 138 kV circuit (38.1 mi.) consists primarily of 1948 vintage wood pole structures with 556 ACSR overhead conductor and currently has 255 open conditions on 126 unique structures including rot top, rot heart, broken insulators and woodpecker/insect damage. From 2015-2018, a total of 7 permanent outages resulted in 167,488 customer minutes of interruption. The Fieldale - West Bassett 138 kV circuit (6.5 mi.) consists primarily of 1948 vintage wood pole structures with 556 ACSR overhead conductor and currently has 48 open conditions on 29 unique structures which is 71% of the circuit. Conditions include rot top, rot heart and woodpecker damage. Fieldale - Stuart 69 kV circuit (19.2 mi.) consists primarily of 1939 vintage wood pole structures and currently has 178 open conditions including broken cross-arms, broken conductor strands, damaged shield wire and woodpecker damage. From 2015-2018, a total of 6 permanent outages and 12 momentary outages were observed. Fieldale - West Bassett #1 69 kV circuit (7.1 mi.) consists primarily of 1926 vintage wood pole structures with 4/0 ACSR and 556 ACSR overhead conductor and currently has 23 open conditions on 21 unique structures including rot top, insect damage, broken ground wire, leaning in-line pole and woodpecker damage. Fieldale - West Bassett #2 69 kV circuit (6.9 mi.) consists primarily of 1962 vintage wood pole structures with 336 ACSR and 556 ACSR overhead conductor and currently has 20 open conditions on 16 unique structures including rot top, broken cross-arms, insect damage, loose knee brace and woodpecker damage. Stuart Station The 69kV CBs D and E are oil filled breakers without secondary oil containment. Oil filled circuit breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. CBs D and E are 2 of 15 in the FKA-72.5-19000-1 model family remaining on the AEP system. This scarcity of sister units makes finding spare parts for these units unviable, and these models are no longer vendor supported. A malfunction report from 2005 documented that CB D was slow to trip on a lightning fault on the Fieldale-Stuart circuit and that CB F at Floyd cleared it; this report also mentioned that this was the second such occurrence of a low trip for CB D. The 69kV CS AA is an S&C 2030-69 model. The S&C 2030 circuit switcher model family has no gas monitor and sister units on the AEP System have experienced malfunctions since 1999; the major ones include gas loss, interrupter failures, and operating mechanism failures. Stuart Substation deploys 48 relays, implemented to ensure the adequate protection and operation of the substation. Currently 45 of the 48 relays (94% of all station relays) are in need of replacement. There are 39 electromechanical type and 3 static type relays with significant limitations in regards to spare part availability in addition to a lack of vendor support and no capability for fault data collection and retention. West Basset Station The 138 kV CB A is a GE FK oil type breaker that has seen 77 fault operations over its in-service life. It is one of only 13 remaining of its model type (FK-439-5000) on the entire AEP system; spare parts availability is a major concern. The 72.5 kV CBs J, K, and L are GE FK oil type breakers as well with CB L seeing 40 fault operations over is in-service life. These are three of only 27 remaining of the their model type (FK-72.5-27000-1) on the entire AEP system; spare parts availability is a major concern. In addition, these four oil filled breakers have much more maintenance required due to their oil handling that their modern SF6 counterparts do not require. The 138/69/34 kV transformer #1 has an upward trending of oil moisture content resulting in decreasing oil dielectric strength. Increasing moisture content is a result of water ingress and/or break down of paper insulation of TF windings. The moisture content has since decreased without improvement to the dielectric strength. Short circuit strength breakdown caused by the amount of thermal through fault events, mostly in excess of 700 C, has lead to major gassing of the unit and carbonization of the insulating paper. West Bassett Substation currently deploys 62 relays, implemented to ensure the adequate protection and operation of the substation. Currently, 55 of the 62 relays (89% of all station relays) are in need of replacement. There are 53 electromechanical and 2 static type with significant limitations in regards to spare part availability and fault data collection and retention in addition to a lack of vendor support. Floyd Station The existing MOAB ground switch design on the high side of transformer #2 needs to be replaced with a circuit switcher to improve the protection scheme and safety of personnel in the station. AEP has been strategically targeting ground switch MOABs for replacement due to the burden that these devices place on Transmission circuit breakers for clearing Distribution Transformer faults.
AEP-2018-AP023 | AEP | PJM West | 2019-01-11 | 2020-03-19 | 2020-05-11 | S2214 |  | Wytheville, Virginia | Wythe 138/69 kV transformer has experienced thermal through fault events, mostly in excess of 700°C, have led to numerous overheating events, steady increases in gasses including high levels of ethylene and ethane, and carbonization of the insulating paper. The oil’s interfacial tension is showing signs of sludge beginning to form due to the carbonization created contaminants. In addition, the moisture content is beginning to climb which has not yet been reflected in a drop in dielectric strength. Wythe circuit breaker F is an FK type oil filled breaker. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. The FK-439-115-3500-3 is no longer vendor supported and is 1 of 2 remaining on the AEP system, making spare parts difficult or impossible to acquire. Wythe circuit breaker M is a CF type oil filled breaker. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. This particular unit has a recorded malfunction related to a broken S.S. line on the maintenance valve and pressure switches. Byllesby circuit breakers B and D are oil filled breakers manufactured in 1952 and 1965 respectively. Both breakers have exceeded the designed number of fault operations (10). These breakers are GE FK type oil breakers with no oil containment. The GE FK type breakers are known to have an internal operating mechanism that are prone to high failure rates. Galax circuit breakers G, F, and H are all GE FK type oil breakers with no oil containment. The GE FK type breakers are known to have an internal operating mechanism that are prone to high failure rates. Circuit Breakers G, F, and H are all approximately 50 years old and have exceeded the designed number of fault operations (10). Jubal Early 138/69kV Transformer has reoccurring bushing damage, dielectric strength breakdown (insulation breakdown) and short circuit breakdown (due to fault events). Recent test reports show oil interfacial tension to be below the minimum acceptable level for a unit of this voltage class. Reduction in oil interfacial tension is related to oil contamination and presence of oxidation byproducts in the oil.
AEP-2018-IM002 | AEP | PJM West | 2018-10-26 | 2019-12-18 | 2020-01-29 | S2167 |  | Pokagon Station circuit breakers | The Pokagon Station CBs J, E, and H are oil filled breakers without oil containment Fault operations: CB E(28), CB H(61) - Recommended (10) Lake Street Station CBs A and H are oil filled breakers without oil containment CB H is a GE FK type which are known to fail violently Fault operations: CB A(24), CB H(13) - Recommended (10) Transformer 1 - 1969 vintage CO2 IEEE level 3 Moisture level high and rising Wood tie supports Niles Station CBs A, B, M, and N are oil filled breakers without oil containment CB M and CB N are GE FK type which are known to fail violently Fault operations: CB A(30), CB B(42), CB N(21) - Recommended (10) Transformer 2 - 1969 vintage CO2 IEEE level 3 Moisture level high and rising Wood tie supports Lake Street - Niles 69kV circuit 1960's wood cross arm construction Poor shielding condition Lakehead Pumping Tap has open conditions on 30% of structures Total open conditions - 54 Lake Street - Niles 34.5kV circuit 1965 wood pole construction Total open conditions - 51 40% of structures with open conditions 97% of line original wood poles Wooden cross arm with cap and pin insulator construction No shield wire
AEP-2018-IM019 | AEP | PJM West | 2019-01-11 |  |  |  |  | Mottville Hydro Station 34.5 kV grounding transformers | Mottville Hydro Station - 1975 vintage 34.5kV grounding transformers carbon dioxide is at IEEE level 3 PCB"s and obsolete bushings Moore Park Station - CB C is a 23 year old 69kV SF6 Breaker (ABB - 72PM31-20) 38 fault operations 38 recorded instances of SF6 additions since 2006 Stubey Road Station - Transformer high side ground switch Sturgis Station - CB A and B 63 year old oil CBs with 37 and 28 fault operations, respectively Replacement parts are very difficult to find for these legacy units Moore Park Tap 69 kV - 1960s vintage wood structures 20 poles identified with structural integrity concerns Part of a three terminal line (~9 miles) Sturgis - Howe (NIPSCO tie) - Vintage 1950s wood cross arm construction with suspended insulators (~3 mi) low capability 4/0 ACSR HMD Station - Permanently jumpered disconnects on main bus Sturgis - Howe (NIPSCO tie) Outage constrained - difficult to outage due to local dependence
AEP-2018-IM023 | AEP | PJM West | 2019-01-11 |  |  |  |  | Deer Creek – Hummel Creek 34.5 kV line condition | Deer Creek – Hummel Creek 34.5kV (11 miles) 1940 wood crossarm construction (age based on age of station) Subject to 16 open A conditions Subject to 17 open B conditions In the past 10 years, 16 structures have had active maintenance performed. This is expected to increase as line ages.
AEP-2018-IM024 | AEP | PJM West | 2019-01-11 |  |  |  |  | Miller Avenue 34.5 kV breakers | Miller Avenue 34.5kV Breakers “A” and “B” 1950 vintage FK oil breaker without containment Fault Operations: CB A(10) CB B(16) – Recommended(10)
AEP-2018-IM026 | AEP | PJM West | 2019-01-11 |  |  |  |  | Grant Tap 138 kV 3-terminal line | Grant Tap 138kV There is a three terminal line about 4 miles outside Deer Creek station.
AEP-2018-IM014 | AEP | PJM West | 2018-10-26 | 2020-09-11 | 2021-01-13 | s2391.1, s2391.2 |  | Gateway & Columbia, Whitley Indiana | Columbia Station Circuit Breakers J 69kV Vintage 1968 GE FKA type oil-filled breakers – without oil containment Fault operations: CB A(95) – Recommended (10) Trip coil failure Spring charging motor failure Gateway Station Circuit Breaker E 69kV 1975 vintage GE FKA type oil-filled breakers – without oil containment Fault operations: CB E(49) – Recommended (10) Three documented instances of breaker failing to close
AEP-2018-OH002 | AEP | PJM West | 2018-10-26 | 2019-11-22 | 2020-01-29 | S2139(s1857 canceled) |  | Customer 138 kV delivery request near Babbitt station | A new customer delivery point has been requested. *Initial load of 150MW with permanent service available by Q1-2020. *Ultimate load for this customer is projected to reach 720MW as early as Q4 2026. *10 MW of distribution construction power for this customer is required in May 2019. 7 MW of distribution construction power for an existing customer planning to expand is also required in 2019. The existing customer has reserved distribution capacity for up to 10 years of expansion activity. As a result, AEP-Ohio has requested a 138kV delivery Point at Babbitt station to serve a “temporary” skid station for up to 10 years. *Additional large customers are in discussions to take service in this area. *Facilities will be designed to accommodate anticipated future load but only facilities required to serve committed load will be constructed.
AEP-2018-OH004 | AEP | PJM West | 2018-10-26 |  |  |  |  | Load requests in the Dublin, OH area | AEP has received requests for increased demand in the Dublin, Ohio area. Analysis shows Bethel - Sawmill 138 kV will be a constraint. Consequent inspection identified clearance violations along the Bethel - Sawmill 138 kV line. AEP has de-rated the thermal capacity of the line to mitigate potential safety issues. Brookside-Sawmill -> N-1-1=127%, N-1=117% Bethel-Brookside -> N-1-1=102%, N-1=92% (N-1-1: Bethel - Roberts 138 kV + Davidson - Roberts 138 kV) AEP believes that the loading issues exist today due to the recent 30% de-rate of the line. Newly connected customer loads are scheduled to ramp up, significantly contributing to area thermal concerns.
AEP-2018-OH005 | AEP | PJM West | 2018-10-26 |  |  |  |  | Loading of the Dublin-Sawmill 138 kV circuit | The Dublin-Sawmill 138kV circuit will experience loading of 116% under N-1-1 conditions involving the loss of Bethel-Davidson 138kV & Davidson-Roberts 138kV circuits. With load growth in the area, we anticipate this line to overload starting in 2022. AEP-Ohio has requested a third 138kV source to Dublin station to maintain acceptable reliability levels for the load at risk. Dublin Station serves 75 MVA of peak demand with minimal load transfer capability. Dublin station serves some critical loads. Newly connected customer loads are scheduled to ramp, significantly contributing to area thermal concerns.
AEP-2018-OH003 | AEP | PJM West | 2018-10-26 | 2020-03-10 | 2020-05-11 | S2213 |  | DOE X-530 | The Ohio Valley Electric Corporation (OVEC) and the US Department of Energy (DOE) are in the process of terminating their connection at Don Marquis. The DOE has informed AEP of its intention to retire its X-530 Substation, adjacent to AEP’s Don Marquis Substation and has requested a new delivery point from AEP at the same location. The new load is anticipated to peak near 38MW.
AEP-2018-OH006 | AEP | PJM West | 2018-10-26 | 2019-11-22 | 2020-01-29 | S2149 |  | Killbuck - South Coshocton 34 kV line condition | The Killbuck - South Coshocton 34 kV line (30.18 mi) was constructed in 1926 using wood pole structures and conductor ranging from 3/0 Copper (23 MVA rating) to 336.4 ACSR (37 MVA rating). There are 144 open A conditions on this line, including rotten cross-arms, burnt/broken insulators, and loose/broken conductor hardware. The Killbuck - South Coshocton 34 kV line has experienced over 1 million CMI over the past three years. The Killbuck - South Millersburg 34 kV (2.59 mi) line was constructed in the 1920'susing wood pole structures with 336.4 ACSR (36 MVA rating). There are 53 open A conditions on this line, including rotten cross-arms, burnt/broken insulators, and loose/broken conductor hardware. The Killbuck - South Millersburg 34 kV line has experienced over 1 million CMI over the past three years. At South Coshocton 69 kV circuit breaker 'K' (fault ops 18), 34.5 kV circuit breakers 'A' (fault ops 3), 'B' (fault ops 7), 'C' (fault ops 72), 'D' (fault ops 0), 'E' (fault ops 0), and 'G' (fault ops 2) are 'FK' oil-filled breaker (vintage 1946 -1973). These oil type breakers have extensive maintenance and oil handling requirements. There is a potential for oil spills during fault operations and maintenance. The FK model is no longer supported by the manufacturer making spare part availability scarce. The South Coshocton 138 kV circuit breaker 'H' has had 11 malfunctions, 3 of which are confirmed to be related to low gas. This HS145-3000 model is prone to low gas malfunctions. The South Coshocton 138/34.5 kV transformer's dielectric strength has declined for the past seven years. Concentrations of CO2 are elevated as well. These conditions indicate that the insulating paper is deteriorating. The South Millersburg 34.5 kV circuit breakers 'A' (fault ops 3) and 'B' (fault ops 21) are 'FK' oil-filled breakers (vintage 1951 and 1953 respectively). These oil type breakers extensive maintenance and oil handling requirements. The FK model is no longer supported by the manufacturer making spare part availability scarce. The South Millersburg 138/34.5 kV transformer has elevated moisture levels for at least seven years with a recent sharp increase. The dielectric strength has corresponding decreased since 2016. Concentrations of CO2 are also elevated Customer Service: Customer #2 Holmes-Wayne Co-op (at Stillwell) and AEP Ohio (at Glenmont) are currently served via a radial 34.5 kV (12.58 mi) line. The Stillwell delivery point has accumulated 1.7 million CMI over the past five years. Over the last 10 years (2008-2017), Stillwell delivery point has averaged nearly 875,000 CMI/year. Customer Service: Customer #3 Licking and Holmes-Wayne members are currently served via a radial 69 kV (24.1 mi) line. The North Liberty to Jelloway radial line is 9.50 miles and the Ripley to Loudonville radial line is 14.16 miles. Their total load is 8.73 MVA and they have experienced 1.13 million CMI over the last three years.
AEP-2018-OH007 | AEP | PJM West | 2018-10-26 | 2020-02-21 | 2020-04-10 | S2199 |  | Condition of 138/34 kV transformers and 34 kV circuit breakers at New Liberty, North Baltimore, and North Findlay Stations | The 138/34kV transformers and 34kV circuit breakers at New Liberty, North Baltimore, and North Findlay Stations have significant asset renewal needs. Between these three stations (17) 34.5kV circuit breakers/ circuit switchers have been identified as needing replacement, 15 of which are oil filled (vintage1950's) and have seen a high number of faults operations. Short circuit capability is also a concern for many of these 34.5 kV breakers at the New Liberty and North Findlay. North Findlay Station: 34.5kV CBs F, G, H, J, K, L 34.5kV circuit switcher BB Transformers #1 and 2 New Liberty Station: 34.5kV CBs C, E, G, H, I, J Transformers #1 and 2 North Baltimore Station: 34.5kV CBs A, B, C, E Morrical Switch 34.5kV CB A Morrical Switch Evaluation of the station has shown the wooden bay structures, the 34.5kV circuit breaker and all existing relaying (electromechanical) at the station are in need of replacement. The following line sections have identified asset renewal concerns and many have seen loading greater than 90% under contingency conditions. New Liberty - North Baltimore 34.5kV: The 10 mile circuit is a combination of 4/0 ACSR and 336 ACSR (circa 1940) with wood structures (Predominately pre-1980's). The line section has 30 open A conditions. North Findlay - North Baltimore 34.5kV #1: The 8 mile circuit identified is predominately 4/0 ACSR (circa 1961) with small portions of 2/0 Copper, 336 ACSR, 556 ACSR, and 795 ACSR. This line has predominantly wood structures (ranging from 1920's - 2000's) with14 open A conditions. New Liberty - Findlay Center 34.5kV: This 3.3 mile line has a combination of 4/0 Copper, 336 ACSR, and 556 ACSR (circa 1934-1964) with wood structures and 10 open A conditions. Whirlpool Extension 34.5kV: This 0.15 miles of rebuild identified is 336 ACSR (circa 1967) with wood structures (circa 1967). Operational Flexibility and Efficiency There is an existing 34.5kV three terminal line at Morrical Switch and hard taps at in the area that increase outages to customers in the area (Totten and Centrex).
AEP-2018-OH008 | AEP | PJM West | 2018-10-26 | 2020-09-11 | 2021-01-13 | s2395.1-.21 |  | Upper Sandusky, OH | There is 1.27 miles of 1/0 Copper and 2.58 miles of 1/0 ACSR conductor on the 69 kV system in the Upper Sandusky area. There are 10 open conditions on the Arlington – Dunkirk 34.5 kV line (~ 7.29 miles) & 29 open conditions on the Forest – South Berwick 69 kV line (~27.6 miles). There is a three-terminal hard tap just west of Hurd Switch. South Carey Switch and North Wharton Switch are both three-terminal lines. West Crawford Switch and Hurd Switch are set in an N.O. position to prevent thermal overloads. The City of Carey has reliability concerns, where both feeds to the city can be lost for a single outage. Hancock-Wood Co-op has reliability and maintenance concerns due to radial loads at Arlington and Blanchard Stations. Arlington – Dunkirk Circuit: Peak Load Impact: 6.57 MW CMI (2015 – 2018): 162,840 Forest – South Berwick Circuit: Peak Load Impact: 7.68 MW CMI (2015 – 2018): 1,713
AEP-2018-OH012 | AEP | PJM West | 2018-10-26 | 2019-12-18 | 2020-01-29 | S2154 |  | 69 kV breakers at Lick station | At Lick substation there are six 69 kV circuit breakers with condition issues. CB's 61,62, 65, 66, 67, and 69 are oil type breakers that were manufactured between 1956 - 1967. There is a potential for oil spills during routine maintenance and fault operations. In addition, spare parts are difficult to obtain. The breakers' fault operation counts are as follows: {61-126, 62-11, 65-26, 66-8, 67-19 and 69-4}. For most of these breakers, the number of fault operations exceed the manufacturers recommended number of 10. There are three 138/69 kV, 18 MVA transformers at Lick. T#1 is a Westinghouse transformer manufactured in 1956. Transformers #2 and #3 are both GE transformers manufactured in 1950. All three transformers have maintenance issues with their LTCs and have significant oil leaks. In addition, loss of two of the transformers can load the remaining transformers tertiary winding above it's rating.
AEP-2018-OH015 | AEP | PJM West | 2018-10-26 | 2020-11-20 |  |  |  | Portsmouth, Ohio | Rarden and Rosemount Stations are connected by a 34.5 kV line with four 34.5/12 kV substations and several distribution customers served directly from the line. The total load served along this 24 mile line is 26/30 MVA (summer/winter). There is a normal-open point near Otway. The area suffers from reliability issues due to the rugged terrain and remote access. Customers have experienced over four million customer minutes of interruption over the past three years. The area's peak load can exceed the source transformers (Rarden and Rosemount). The 336 AAC conductor has already been overloaded (115% on 2014). The two 69-34.5 kV transformers at Rarden are protected with high-speed ground switches which can cause through-faults on the transmission system.
AEP-2018-OH016 | AEP | PJM West | 2018-10-26 | 2019-11-22 | 2020-01-29 | S2140 |  | Strasburg, Ohio | The Beartown- West Wilmont 69kV section 10.5 miles long and serves 1 AEP Ohio distribution station and 2 1 Holmes-Wayne Co-op station in northeast Ohio. Over the past several years, the circuit has experienced below-average reliability. For the 2017-2018 YTD period, it has experienced 7 sustained outages, an additional 8 momentary interruptions, and 2 emergency repair incidents on the entire circuit. The majority of the outages were due to T-Line structural issues and forestry. The line section consists of primarily 336 ACSR (1962-64 vintage); it is entirely wood pole construction, with the majority being installed in the 1960’s. The section has a reported CMI of 2.0M between 2014 – 2018 and currently has 52 open conditions (25 Category A, 25 Category B, 5 Forestry). Examples of the conditions include: rotted poles, missing ground-leads, and damaged conductor. During the 2010-2018 period, 112 prior conditions were repaired/addressed on the circuit as a whole.
AEP-2018-OH017 | AEP | PJM West | 2018-10-26 | 2020-03-19 | 2020-05-11 | S2215 |  | Putnam County, Ohio | Continental - Roselms 69 kV is a 18 mi radial circuit serving ~10.6 MVA load. The customers served from this radial line have experienced 2.1 million customer minutes of interruptions over last 5 years. These radial loads are not automatically transferable. Any maintenance on this line results in outages to multiple stations. ajority of the line has 4/0 ACSR conductor with a 2 mi section with 795 ACSR. This circuit has 89 open conditions. Most of the 258 structures on this circuit are 1960s and 1970s wood pole vintage with rotting issues.
AEP-2018-OH020 | AEP | PJM West | 2019-01-11 | [5 empty] | Hilliard Station 69kV: CB 61, CB 62, and CB 63 are 1960's vintage 69kV oil-filled breakers. Oil type breakers are difficult to maintain due to oil handling requirements, and have had a number of fault operations: CB 61 (15), CB 62 (21) and CB 63 (31). 105 of the 119 relays are electromechanical relays. EM relays have limited spare part availability, no vendor support, no SCADA functionality, and no fault data collection ability. The RTU is obsolete and does not meet current standards. The structure steel is deteriorating due to rust and the foundation supporting the steel shows severe cracking. Trabue Station 138/69kV: The 1960"s vintage, 138/69 kV, 115MVA Transformer #3 is recording elevated gas levels due to through fault conditions. 60 of the 86 relays are electromechanical relays. EM relays have limited spare part availability, no vendor support, no SCADA functionality, and no fault data collection ability. Galloway Station 69kV: 104 of the 122 relays are of the electromechanical type. EM relays have limited spare part availability, no vendor support, no SCADA functionality, and no fault data collection ability. The RTU is obsolete and does not meet AEP standards. The structure steel is deteriorating due to rust and the foundation supporting the steel shows severe cracking. Beatty-Galloway 69kV: The total circuit (~ 8 mi) currently has 51 open A conditions (structure, conductor, shielding grounding, hardware, and other) with a number of deteriorated overhead structures. Beatty Station 138/69kV: Three 1960"s vintage 69 kV oil breakers, CB 63, CB 64, and CB 65, show signs of bushing damage, lack of available repair parts, and high PCB content. Oil type breakers are difficult to maintain due to oil handling requirements, and have had a number of fault operations: CB 64 has seen 34 fault operations. 1960"s vintage, 138/69 kV 50 MVA transformers #2 & #4 are showing signs of short circuit strength breakdown due to the amount of through fault events, dielectric strength breakdown, and bushing damage (bushings). Transformer #2 also has a high levels of dissolved gas in the oil.
AEP-2018-OH024 | AEP | PJM West | 2018-11-29 | [5 empty] | The 138kV riser is currently the Most Limiting Series Element on the 765/138 kV transformer at Maliszewski, reducing the summer normal rating by 170MVA. With customer load requests in the area, we anticipate this limitation overloading in the future. A transformer outage is already scheduled so utilizing already mobilized crews to save on costs in the long run would be desirable.
AEP-2018-OH018 | AEP | PJM West | 2018-11-29 | 2020-06-19 | 2020-09-15 | s2282 |  | Columbus, Ohio | * A study of the current physical loading capability of the structures along the Astor-Shannon-Groves & Shannon - Bixby 138 kV circuits revealed that many of the poles are currently overloaded under NESC Heavy Loading Conditions. Additionally, the line structures are unable to handle the addition of telecom fiber, which is needed to improve communications in this area. Existing NESC Heavy Loading Conditions: * 36% of poles on the Astor-Bixby 138 kV circuit show overloading. * 29% of poles on the Bixby - Shannon 138 kV circuit show overloading. * 20% of the poles on the Shannon - Refugee 138 kV circuit show overloading. * 58% of poles on the Refugee - (Future) Brice 138 kV circuit show overloading. * 35% of poles on the (Future) Brice - Astor 138kV circuit show overloading. * Primarily 1952 wood poles (57% of total line) * Conductor is all from 1952 * 43 (out of 155) structures on the circuit have at least 1 open condition (28%), with a total count of 63 open conditions. 23 reported closed conditions - 1 forestry, 4 conductor, 18 structure * No outage history (0 CMI/CI) * The Astor-Groves-Shannon 138 kV circuit is a three-terminal line, which limits sectionalizing and can cause mis-operations and over tripping. * Astor 138 kV Station has ground switch MOAB’s on both 138/13 kV transformers. Ground switch MOABs cause intentional high side faults, which can damage nearby equipment.
AEP-2018-OH029 | AEP | PJM West | 2019-01-11 | [5 empty] | The Fisher-Hall-Wilson 138kV circuit is a three terminal line. Three-terminal lines cannot be protected adequately and lead to mis-operations including over tripping. At Wilson Road station, 138kV CB’s 2, 3, 4, 5, 6, 7, 8, & 9 (vintage1960-1970), 46 kV cap switcher AA (vintage 1995), and 40kV CB’s 30 & 35 (vintage 1956) are all oil type interrupting devices. Oil type equipment is difficult to maintain due to the oil handling requirements and due to environmental risk associated with spills that are common. In addition, some of these devices have exceeded the manufactures recommended number of fault operations 40kV CB 35 (55) and 138kV CB 4 (17). 40kV is considered to be an obsolete voltage technology because of lack of replacement/repair parts and lack of vendor support. McComb station is served from two 138kV sources, one of which relies on an underground oil filled pipe type cable. This is a reliability concern because any significant outage will likely require several months to repair, leaving the station radialized. We have experienced several prolonged outages of oil filled cables. These cables are only manufactured by a single manufacturer with a lead time of 8-12 months. Two 50MVA transformers at McComb are protected by ground switch MOABs which can cause damage nearby equipment when they operate. The 1.7 mile Briggsdale-McComb 40kV line (vintage 1973) has 8 open conditions including hardware, shielding/grounding, and forestry. The 5.19 mile Briggsdale-Wilson 40kV line (vintage 1935 – 2011) has 87 open conditions including structures, conductor, shielding/grounding, hardware, and forestry.
AEP-2018-OH027 | AEP | PJM West | 2018-11-29 | 2020-03-19 | 2020-05-11 | S2224 |  | Athens Area Improvements | Equipment Material / Condition / Performance / Risk: * Elliott 138 kV circuit breaker 102 (vintage 1956) is an oil type breaker recommended for replacement due to bushing damage, reliability, and lack of spare part availability. * Elliot 69kV circuit breakers 61, 66, and 67 (vintage 1972) have experienced the following numbers of fault operations: CB-102 (38), CB-67 (10), CB-66 (40), and CB-61 (1). These breakers are oil type breakers recommended for replacement due to reliability and lack of spare part availability. * Strouds Run 69kV circuit breakers 63 and 66 (vintage 1969-1973) are oil breakers recommended to replace due to reliability and lack of spare part availability. Maintenance has become more difficult due to the oil handling required to maintain them. They have experienced the following fault operations: CB 63 (24), CB 66 (0). * Strouds Run 138kV Circuit switchers “CS-TR1” and “CS-TR2” are Mark type switchers. Mark switchers are being recommended for replacement system wide due to their inability to coordinate with modern relaying packages. Circuit switchers have experienced the following fault operations: CS-TR1 (17), CS-TR2 (18). * Strouds Run 138/69 kV 33.6MVA transformer #1 (vintage 1972) is also showing significant signs of deterioration. Drivers for replacement include dielectric strength breakdown, short circuit strength breakdown, and bushing damage. * Clark Street 69 kV circuit breakers 61 and 64 (vintage 1968) are oil filled breakers that have been recommended for replacement due to oil handling requirements, no longer has vendor support, lacks sufficient spare part availability, and has a history of malfunctions. The breakers have had the following fault operations: CB 61 (8) and CB 64 (15). Equipment Material / Condition / Performance / Risk: * The Elliot - Lee 69kV 8 mile, 69 kV line (vintage 1974) was constructed using wood pole structures with 336.4 KCM ACSR 18/1 conductor (73 MVA rating). * There are 106 open A conditions on this line, including rotten structures, burnt/broken insulators, and loose/broken/sagging conductor sections, improperly installed shield wires and woodpecker damaged structures. * These stations still have the following amount of electromechanical relays employed: Elliot (29), Strouds Run (78), Clark Street (25). EM relays have limited vendor support, lack SCADA functionality, and don’t offer fault data collection. Operational Flexibility and Efficiency: * The Crooksville - Poston - Strouds Run 138kV circuit is a three-terminal line, which limits sectionalizing and can cause mis-operations and over tripping. * The Dexter - Elliot - Poston 138kV circuit is a three-terminal line, which limits sectionalizing and can cause mis-operations and over tripping.
AEP-2018-OH030 | AEP | PJM West | 2019-01-11 | 2021-02-17 |  |  |  |  | The 27-mile 69kV Portsmouth-Ironton line (vintage 1915) uses wood pole structures with variety of conductors, mostly 2/0 Cu (40 MVA rating). A 11.9 mile section between Millbrook Park and Franklin Furnace has 73 open A conditions, including rotten cross-arms, burnt/broken insulators, and loose/broken conductor hardware. The Millbrook Park-Franklin Furnace-Argentum line is a 3-terminal line. Three-terminal lines cannot be adequately protected due to the complexity of coordination, which, causes misoperations including over-tripping. The Millbrook Park-North Haverhill-Argentum circuit is protected by an impedance based Directional Comparison Blocking (DCB) pilot system, which cannot adequately protect a three terminal lines. Over the past several years, the Millbrook Park-Argentum-North Haverhill circuit has experienced reliability issues including 5 sustained outages and 21 momentary outages. The Texas Eastern Substation serves a peak load of 26 MW via a 2.1-mile radial line from East Wheelersburg. Also, K.O. Wheelersburg is a 1.2 MVA 69 kV retail load served off a 1.3-mile radial line. These radial loads are at risk of extended outages for line maintenance or repair. At Sciotoville, CBs A and B are both oil type breakers with 16 and 10 fault operations respectively. This particular model has no spare parts and a history of poor reliability. Sciotoville has a ground switch MOAB on the transformer. Ground switch MOAB’s cause intentional high side faults to clear the transformer faults which cause damage to and reduction in life of nearby equipment. Sciotoville and Wheelersburg currently have 8 (of 10) and 10 (of 10) electro-mechanical relays respectively. EM relays have no spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability.
AEP-2018-OH032 | AEP | PJM West | 2019-01-11 | 2/21/2020, 3/10/2020,5/12/2020 | 2020-08-06 | S2270 |  | Cameron Customer Service | A customer has requested new service west of Cameron, West Virginia. The forecasted peak demand is 30 MW initially, with long-term prospects of 90 MW. With the addition of this customer load, plus the new customer load on S2097 (AEP-2019-OH006), the Wayman-Gosney-Nauvoo Ridge 138kV radial line has an MVA-mile demand of 1142 896, far exceeding AEP’s guideline of 75 MVA-miles. The MVA-mile demand that exists today on the Wayman-Gosney Hill 138kV circuit is 313 without any new load additions. After additional DNH study by PJM, a generation deliverability overload was found at Gosney Hill 138kV station on the Gosney Hill- Nauvoo Ridge 138 kV line for loss of the Kammer-Panhandle 500 kV line and the Kammer 765/500 kV transformer ('AEP_P1- 3_#8975_05KAMMER 765_200‘, 'AEP_P1-2_500-1‘).
AEP-2018-OH036 | AEP | PJM West | 2018-10-26 |  |  |  |  | Moreland - West Wilmont, Roseville, OH | The Moreland- West Wilmont 69kV section is 17.7 miles long and serves 1 AEP Ohio distribution station and 1 Holmes-Wayne Co-op station in northeast Ohio. Over the past several years, the circuit has experienced below-average reliability. For the 2017-2018 YTD period, it has experienced 7 sustained outages, an additional 8 momentary interruptions, and 2 emergency repair incidents on the entire circuit. The majority of the outages were due to T-Line structural issues and forestry. The line section consists of primarily 4/0 copper conductor (1940 vintage) and 336 ACSR (1962-64 vintage); it is entirely wood pole construction, with the majority being installed in the 1960’s or earlier. The circuit has a reported CMI of 2.0M between 2014 – 2018 and currently has 166 open conditions (152 Category A, 11 Category B). Examples of the conditions include: rotted poles, missing ground-leads, and damaged conductor. During the 2010-2018 period, 112 prior conditions were repaired/addressed on the circuit as a whole. Also, at the North Fredericksburg station, the two 69kV line switches can only be operated when the line is de-energized, due to issues with the vacuum bottles and obsolete design.
AEP-2018-OH035 | AEP | PJM West | 2018-10-26 | 2020-05-22 | 2020-08-06 | S2271 |  | Walhonding | Customer #1: A recent customer service request of 2.5 MW has been made on the Killbuck – South Coshocton 34.5 kV circuit.
AEP-2019-AP001 | AEP | PJM West | 2019-02-20 | 2020-10-16 |  |  |  | Bim Station | Bim 69 kV * Breaker “D” * 1967 FK oil type breaker without containment * Fault operations: 369, recommended 10 operations * Cap Switchers “AA” and “BB” * SC-2030 type * No gas monitoring * Sister units have experienced numerous gas and interrupter failures Bim 46 kV * Breakers “A”, “B”, “C”, and “E” * 1967 FK oil type breakers without containment * Fault operations: CB A (85), CB B (14), CB C (131), CB E (63), recommended 10 operations Bim Station * Existing Gr. SW. MOAB configuration creates faults in the station; known safety hazard in legacy station designs * Transformer Bank #1 138/69/46 * Oil leaking at a steady rate * Deteriorating wooden crossties, obsolete arresters and bushings, LTC is not in adequate condition * Cooling system and controls need replaced * GND Bank * Interfacial tension in all three units has been on the decline or at sustained low levels for around 15 years, indicating the development of sludge which can impede oil circulation/cooling * Rising/Sustained high moisture content has resulted in degrading/sustained low levels of dielectric strength * Obsolote arresters/bushings, deteriorating wooden crossties * Cooling system/controls need replaced
AEP-2019-AP002 | AEP | PJM West | 2019-02-20 | 2020-07-17 | 2020-10-21 | s2347 |  | Mullens Station | Mullens Station * Transformer Bank #4 138/46 kV * Short circuit strength breakdown caused by the amount of high energy electrical through fault events * Numerous gases are at the IEEE level 2 condition level with acetylene and ethylene being at the highest condition level 4, which negatively impacts the oil dielectric * Major carbonization of the insulating paper as occurred from these numerous through fault events, indicating that this unit is near the end of its useful life * There is a bad fan on transformer #4, on the bottom of cooling group 2 * Grounding Bank #3 * Upward trending of oil moisture content resulting in downward trending to the oil dielectric strength * Increasing moisture content is a resultant of water ingress and/or break down of paper insulation of TF windings * Short circuit strength breakdown caused by the amount of thermal through fault events * Existing Gr. SW. MOAB configuration on the 138/46 kV and 138/34.5 kV transformers create faults in the station; known safety hazard in legacy station designs * 63 of the 74 relays in the station (85% of all station relays) are of the electromechanical type which have significant limitations with regards to fault data collection and retention * 13.2kV CBs R & S at are oil filled breakers without oil containment
AEP-2019-AP005 | AEP | PJM West | 2019-02-20 | [5 empty] | The 138/12 kV Transformer #3 at Fremont station is 1971 vintage and is showing dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). 138/69 kV Transformers #1 and #2 at Fremont station are 1957 vintage and show significant signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults).
AEP-2019-AP003 | AEP | PJM West | 2019-02-20 | 2019-11-22 | 2020-01-29 | S2141 |  | Lynchburg, VA | * The 1959 vintage 138/69/34.5 kV transformer #1 at South Lynchburg Substation has elevated levels of carbon dioxide which began increasing in 2004. Additionally, the interfacial tension is steadily decreasing and the oil power factor is steadily increasing indicating that the oil insulation is beginning to degrade as well. This data proves that the transformers insulation is aged and has degraded. * The 34.5 kV Grounding Bank was manufactured in 1954 and has high concentrations of combustible gases, specifically CO and CH4, due to various thermal faults and electrical discharges. Short circuit breakdown caused by the amount of through fault events, some greater than 700 degrees Celcius has contributed to the deterioration of the bank. * 12 kV CBs P, L, K, N, M, and R are oil breakers * Number of fault operations: P (44), L (42), K (152), N (132), M (34), R (135) * 34.5 kV CB F has 31 fault operations * 34.5 kV CB G has 63 fault operations
AEP-2019-AP006 | AEP | PJM West | 2019-03-25 | 2019-11-22 | 2020-01-29 | S2142 |  | Montgomery County, VA | Craig-Botetourt Electric Cooperative (CBEC) requested a new delivery point from AEP to be located in Montgomery County, Virginia. The new station will serve approximately 10 MVA.
AEP-2019-AP007 | AEP | PJM West | 2019-03-25 | 2020-03-19 | 2020-05-11 | S2219 |  | Letcher County, Kentucky | Fleming Station * 138/69 kV Transformer #1 * 1984 vintage transformer. * Shows signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). * Reports from the field show active oil leaks from the gaskets and slight leaks from the unit’s welds. * Utilizes a ground switch MOAB scheme as part of the high side transformer protection. * 69/12 kV Transformer #3 * 1979 vintage transformer. * Shows signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). * 69 kV Circuit Breakers B, E, and F * CF-48 type oil breakers. (1965, 1968, and 1967 vintage) * These are oil breakers are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. * Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturers recommendations. * Have experienced 114, 26, and 68 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. * This circuit breaker model family has experienced numerous documented mechanism bearing issues and failures within the AEP population. CBs B & F have had malfunction records indicating a failure to properly latch during operation. Fleming Station * S&C Circuit Switcher ‘AA’ * No gas monitor, sister units on the AEP system have a history of gas loss, interrupter failures, and operating mechanism failures. * 12 kV Circuit Breakers C and D * ES type oil breakers. (1979 vintage) * These are oil breakers that have become more difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. * These are oil breakers that have become more difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. * Have experienced 36 and 19 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. * 69 kV Circuit Breaker A * 72EPB-31.5-20 SF6 type breaker with known gas leaks. (1990 vintage) * 18 malfunction records for this breaker since 2009 related to low gas alerts. * 1 of 12 remaining breakers of this type on the AEP system.
AEP-2019-AP008 | AEP | PJM West | 2019-03-25 | 2019-12-18 | 2020-01-29 | S2166 |  | Lakin - Racine Rebuild | Racine 69 kV circuit breaker B * CG-48 oil type breakers that was manufactured in 1980. * Oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance which can be an environmental and safety hazard. * Experienced 43 fault operations, exceeding the manufacturer's designed number of fault operations of 10.
AEP-2019-AP010 | AEP | PJM West | 2019-04-23 | 2020-07-17 | 2020-10-21 | s2348 |  | Chemical Area Project | * South Charleston 46 kV CBs A and B are 460G-3000 oil filled breakers. * Oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance which can be an environmental and safety hazard. * These are the last 2 circuit breakers in the 460G-3000 CB model family on the AEP system, making spare parts difficult or impossible to obtain. * Chemical – South Charleston 46 kV #1 (~0.5mi) currently has 9 open conditions on 8/8 structures. * The majority of the circuit is constructed with 1950s wood structures and lattice structures. * The conditions include rot shell, insect damage and heavy rust.Chemical – South Charleston 46 kV #2 (~0.5mi) currently has 16 open conditions on 9/9 structures. * The majority of the circuit is constructed with 1950s lattice and wood structures. * The conditions include rot and heavy rust and rot shell.
AEP-2019-AP011 | AEP | PJM West | 2019-04-23 | 2019-12-18 | 2020-01-29 | S2165 |  | Winfield, West Virginia | 69 kV circuit breakers F and G at Bancroft station are CF-48 oil type breakers that were manufactured in 1965. * Oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance which can be an environmental and safety hazard. * Breakers F and G have experienced 55 and 70 fault operations, exceeding the manufacturer's designed number of fault operations of 10.
AEP-2019-AP012 | AEP | PJM West | 2019-06-17 | 2019-11-22 | 2020-01-29 | S2143 |  | Danville, VA Area | Danville, VA Area Pilot Wire Several documented mis-operations have occurred related to defective and disabled pilot wire relaying between Danville, East Danville and the local 69 kV network. Pilot wire maintenance is a known safety concern especially during poor weather conditions. Elimination of pilot wire in the Danville area will address ground splice concerns, pilot wire cabinet access issues and low hanging pilot wire on poles. Corrective maintenance continues to be a concern due to the lack of spare relay components and it being an obsolete technology. Due to the abnormal conditions and overall age of the pilot wire in the Danville area, mis-operations have impacted several large industrial customers. East Danville Station 138 kV Circuit Breakers L and M 12 malfunction records indicating low SF6 gas during cold weather conditions with continued maintenance required Have experienced 19 and 49 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. 138 kV Circuit Breaker P CB P is FK type oil breaker (1955 vintage) Oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. 69 kV Circuit Breakers F and H FK type oil breakers (1965 vintage) Malfunction on CB H for an air leak on the control valve Have experienced 46 and 78 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. 69/12 kV T#3 High side MOAB Ground Switch Tapped off of East Danville-US Gypsum 69 kV line, not currently tapped off bus Goodyear Station 69 kV Circuit Breakers A, C and D FK type oil breakers (1959, 1973 and 1972 vintage respectively) Oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. Have experienced 18, 9 and 7 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. Customer metering CTs and PTs are over 50 years old and accuracy class below recommended US Gypsum Station Customer metering CTs and PTs are over 50 years old and accuracy class below recommended 69 kV Circuit Breaker A FK type oil breaker (1966 vintage); experienced 21 fault operations Rigis Station 138/69 kV T#1 High side MOAB ground switch protection Corning Glass Station 69 kV Circuit Breaker B FK type oil breaker (1966 vintage); experienced 80 fault operations Circuit Switchers A and AA S&C 2030-69, no gas monitor, model family has numerous documented malfunction records concerning gas loss and interrupter failures Danville Station 69 kV Circuit Breaker J FK type oil breaker (1966 vintage)
AEP-2019-AP013 | AEP | PJM West | 2019-06-17 | 2019-12-18 | 2020-01-29 | S2165 |  | Nitro, West Virginia | Bancroft – Nitro 69 kV (~7.6 miles) Majority of the circuit is constructed with 1930s (46/97, 47%) and 1960s (20/97, 21%) wood structures The circuit currently has 27 open conditions Structure loading does not meet current NESC standards. The conductor is greater than 65 years old, and exceeds the recommended lifespan. Grounding on this line does not meet current standards. Between 2015-2018 the circuit experienced 2 momentary and 1 permanent outage resulting in approximately 800k customer minutes of interruption Nitro – Turner 69 kV (~7.3 miles) Over half of the circuit is constructed with 1920s wood structures (51/75 structures, 68%) The circuit currently has 60 open conditions Approximately half of the line is not shielded. From 2015-2018 the circuit has experienced 8 momentary and 6 permanent outages resulting in approximately 130k customer minutes of interruption
AEP-2019-AP014 | AEP | PJM West | 2019-05-20 | 2019-12-18 | 2020-01-29 | S2165 |  | Nitro, West Virginia | *Turner 46kV CB-O *One of only six remaining of the 72EPB-20-12 model on the AEP system. *These model types have historically exhibited bad gas leaks, bushing failures, and CT cores getting wet. *Since 2015, there have been 25 documented malfunction records on this unit in regards to low SF6 gas levels. *Turner 138/69 kV Bank #5 *Recently de-rated due to the loss of a cooling pump that cannot be replaced. *This unit could experience an increasing number of overheating events with the potential to cause damage to internal components *Moisture content has been rising for a number of years but more severely over the past 11. * The rise in moisture content correlates to a significant drop in dielectric strength and rising power factor level for the oil. *All three high side bushings are of the Type U design that have extensive manufacturer alerts related to catastrophic failures. *Turner GND Bank #7 *Ethane concentrations in this unit increased drastically in 2018, CO2 levels have increased in 2018 as well. The relative gas concentrations are indicative of numerous overheating events. *Decreasing interfacial tension since 2002, this transformer has likely developed sludge in the oil from deteriorating internal components. The presence of this sludge is likely what is impairing proper oil circulation and contributing to the number of overheating events. *Increase in moisture levels, correlating with an increased power factor and also indicative of oil degradation. *The current station configuration has each bank located on a 138kV Bus with only a MOAB on the high side. A transformer fault on any of the transformer banks will cause a momentary outage of one of the 138kV Buses. *Turner Station Control House *Has asbestos and lead paint and existing water leaks. *Steps leading up to control house are hazardous to anyone entering station. *Currently, 61 of the 95 relays (64% of all station relays) are in need of replacement at Turner Station *There are 55 of the electromechanical which have significant limitations with regards to fault data collection and retention. *There are 5 ABB DPU microprocessor type relays. *ABB DPU relays pose a safety risk to persons performing breaker operation because the DPUs are mounted directly on the circuit breaker without a delay for opening and closing the breaker. *An additional microprocessor is an RFL that utilizes obsolete firmware and is no longer vendor supported.
AEP-2019-AP015 | AEP | PJM West | 2019-08-29 | 2020-03-19 | 2020-05-11 | S2225 |  | Hernshaw Area Project | *A customer station is currently served off a hard tap on the Belle – Cabin Creek – Marmet Hydro 46 kV circuit.*Hard taps are difficult to maintain due to required outages or temporary jumper configurations in lieu of a switch.*Hard taps can also result in extended outages to customers due to the inability to sectionalize faulted facilities.
AEP-2019-AP016 | AEP | PJM West | 2019-06-17 | 2019-11-22 | 2020-01-29 | S2144 |  | Trap Hill Area Project | Trap Hill Station serves approximately 20 MVA of load from a 6 mile radial thus exceeding AEP’s threshold for looped service of 75 MVA-mile. Long radial line or radial lines serving a significant amount of load are concerning as they age due to: Maintenance of radial facilities being difficult due to the required customer outages. Radial delivery points resulting in extended outages to customers for any loss of the feed due to the lack of looped service and transferability of the load. Bolt Tap 138 kV is a hard tap off the Baileysville – Sundial 138 kV #1 circuit. Hard taps are difficult to maintain due to required outages or temporary jumper configurations in lieu of a switch. It can also result in extended outages to customers due to the inability to sectionalize faulted facilities. Dameron 46 kV CB-A Oil filled ITE 69KA-2500-12D type breaker, 1 of 13 of this type of model left on the AEP system. These types of breakers experience issues with their parts and maintenance costs due to lack of vendor support. Oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance which could pose an environmental and safety hazard. Dameron 46 kV Cap switcher AA S&C 2030-69 unit that has no gas monitor and sister units on the AEP system have experienced 62 malfunctions since 1999. Major events include gas loss, interrupter failures, and operating mechanism failures. Dameron 138/46 kV Bank #1 Rising moisture, carbon monoxide (CO), and carbon dioxide (CO2) levels which indicate a deterioration of the insulating paper. Sustained low levels of interfacial tension also ties to insulation degradation and is an indication of sludge formation. Sludge can impede oil circulation and generate numerous instances of overheating, further accelerating the declining health of the unit. The current MOAB/Ground SW configuration on the high side. Dameron grounding transformer 99 year old unit in which all 3 phases are facing similar condition issues. Sustained elevated moisture levels and power factor have led to decreasing dielectric strength. Sustained low levels of interfacial tension is an indication of sludge formation. Sludge can impede oil circulation and generate numerous instances of overheating, further accelerating the declining health of the unit. Dameron Substation currently deploys 41 relays, implemented to ensure the adequate protection and operation of the substation. Currently, 36 of the 41 relays (88% of all station relays) are in need of replacement. There are 33 of the electromechanical type and 1 static type which have significant limitations with regards to fault data collection and retention. In addition, 2 microprocessor relays were commissioned in 1997 and 2005, indicative of obsolete firmware that is no longer vendor supported. Bolt 46 kV cap switcher AA 1 of 15 remaining VBM-69 types left on the AEP system. These types of cap switchers perform poorly in cold weather and replacement parts are known to be expensive when they are available per the TFS obsolete list. Bolt 46 kV grounding transformer All 3 phases are facing similar condition issues as listed. Sustained elevated moisture levels and power factor have led to decreasing dielectric strength. Sustained low levels of interfacial tension is in indication of sludge formation, in which sludge can impede oil circulation and generate numerous instances of overheating, further decreasing the health of the unit. Bolt 138/46 kV XFR Moisture levels and power factor have been on the rise since 2004. These increases correspond to decreasing dielectric strength levels seen over the same period. The most probable causes of moisture in oil for this unit are paper breakdown (aging), moisture ingress through gaskets, and leaks (main tank; pumps; etc.). Interfacial tension has been at a sustained low level since 2008; this is an early indication of the development of sludge from contaminates in the oil. Over time, the sludge can further impede the ability of oil to properly circulate, potentially leading to more frequent unit overheating.
AEP-2019-AP017 | AEP | PJM West | 2019-06-17 | 2020-02-21 | 2020-04-10 | S2188 |  |  | Beaver Creek – McKinney #1 46 kV Circuit From 2016-2018, the approximately 24.6 mile Beaver Creek – McKinney #1 46 kV circuit has experienced 22 outages. The circuit is comprised of 152 structures, the majority of which are wood structures dating back to 1929 (22/152, 14%) and 1949 (61/152, 40%). There are 142 open conditions along the 24.6 mile long line. These include damaged poles and cross-arms, conductor/shield wires, and guy anchor/knee/vee braces. Hays Branch Station Hays Branch serves a ~30 MW gas compressing operation that is currently radially fed from a ~8.25 mile line out of Morgan Fork station. Saltlick Station Saltlick serves an EKPC co-op that is currently radially fed off the Beaver Creek – McKinney 46 kV circuit. Spring Fork Spring Fork station serves KPCo distribution customers and is currently radially fed off the Beaver Creek – McKinney 46 kV circuit. Consolidation Metering Consolidation Metering station serves a mining operation and is currently radially fed off the Beaver Creek – McKinney 46 kV circuit.
AEP-2019-AP019 | AEP | PJM West | 2019-05-20 | [5 empty] | *West Kingsport 34.5 kV *34.5 kV Circuit breakers A, C, and F *FK type oil breakers. (1955, 1955, and 1966 vintage) *These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. *Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturer’s recommendations. *Have experienced 26, 26, and 21 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10.
AEP-2019-AP020 | AEP | PJM West | 2019-05-20 | [5 empty] | *34.5 kV Circuit breakers A, B, and N *FK type oil breakers. (1956, 1956, and 1954 vintage) *These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. *Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturer’s recommendations. *Have experienced 40, 34, and 15 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. *S&C Circuit Switcher ‘AA’ *No gas monitor, sister units on the AEP system have a history of gas loss, interrupter failures, and operating mechanism failures.
AEP-2019-AP018 | AEP | PJM West | 2019-05-20 | 2020-03-19 | 2020-05-11 | S2226 |  | Mercer County, West Virginia | *Speedway 138 kV Tap *There are 34 open conditions associated with the 1960s wood structures that comprise the 7.3 mile Speedway Tap that serves Speedway station. These conditions include damage due to woodpecker holes, damaged poles, and corroded cross-arms. *Glen Lyn – Hatcher 138 kV Line Section *The Glen Lyn – Hatcher 138 kV line section utilizes double circuit lattice structures and conductor installed during the 1920s. The structures, conductor, hardware, and insulators on the line are displaying issues associated with their age. *Speedway Station *Speedway station is currently radially served off the ~7.3 mile Speedway 138 kV Tap. *Speedway station has 20 MW of nontransferable load (25 MW peak).
AEP-2019-AP019 | AEP | PJM West | 2019-05-20 | 2020-12-18 |  |  |  |  | *West Kingsport 34.5 kV *34.5 kV Circuit breakers A, C, and F *FK type oil breakers. (1955, 1955, and 1966 vintage) *These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. *Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturer’s recommendations. *Have experienced 26, 26, and 21 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10.
AEP-2019-AP020 | AEP | PJM West | 2019-05-20 | 2020-12-18 |  |  |  | Sullivan County, Kingsport, Tennessee | Cumberland Station 34.5 kV Circuit breakers A, B, and N FK type oil breakers. (1956, 1956, and 1954 vintage) These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturer’s recommendations. Have experienced 40, 34, and 15 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. S&C Circuit Switcher ‘AA’ No gas monitor, sister units on the AEP system have a history of gas loss, interrupter failures, and operating mechanism failures.
AEP-2019-AP021 | AEP | PJM West | 2019-05-20 | 2020-04-20 | 2020-06-15 | S2249 |  | Sullivan County, Tennessee | *Holston Station *138/34.5 kV Transformer #1 *Manufactured in 1979. *Showing signs of dielectric breakdown (insulation), accessory damage (bushings/windings), and short circuit breakdown (due to through faults). *Currently tied directly to 138 kV bus #1 via a MOAB on high side. *34.5/23-2.4 kV Transformer #8 (GND Bank) *Manufactured in 1954. *Showing signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). *Capacitor switchers ‘BB’ and ‘CC’ *Capacitor switchers ‘BB’ and ‘CC’ at Holston station are Mark V model which no longer support modern relaying packages. *Mark V’s have been historically prone to mechanism failures and are being replaced system wide where possible. *34.5/23-2.4 kV Transformer #9 (GND Bank) *Manufactured in 1953. *Showing signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). *34.5 kV Circuit breakers E, F, and U *FK type oil breakers. (1959, 1955, and 1950 vintage) *These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. *Other drivers include damage to bushings and the breakers have experienced 2,19, and 7 fault operations respectively. The manufacturer’s recommendation for this type of break
AEP-2019-AP022 | AEP | PJM West | 2019-05-20 | 2020-03-19 | 2020-05-11 | S2220 |  | AEP-2019-AP022 | AEP Kentucky Power Distribution has requested a new distribution service out of the existing Cedar Creek Station located in Pikeville, Kentucky. Winter projected load is 12.5 MVA.
AEP-2019-AP023 | AEP | PJM West | 2019-07-24 | 2019-11-22 | 2020-01-29 | S2145 |  | Fayette County, WV | Amos – Hopkins 138 kV (~31.37 miles) – Majority of the circuit is constructed with 1920s lattice structures * The lattice towers used for this line are approximately 94 years old. Structure loading does meet the NESC 250B, 250C and 250D standards for all structures that were analyzed. * Steel lattice towers and hardware are currently exhibiting medium to heavy rust – The shield wire and conductor for this line is 94 years old. Current shielding for the majority of the line does not comply with current standards.
AEP-2019-AP024 | AEP | PJM West | 2019-07-24 | 2020-02-21 | 2020-04-10 | S2189 |  | Wyoming/McDowell Counties, WV | Baileysville – Hales Branch 138 kV (~27.8 miles) * Majority of the circuit is constructed with 1970s wood structures. * Between 2015-2018 the circuit experienced 24 momentary outages. * All momentary outages are attributed to lightening, insufficient shielding and aging towers as the structures, conductor, hardware, and insulators on the line are displaying issues associated with their age * The circuit currently has 54 open conditions * Open conditions include: Rotten Tops, Woodpecker damage, Split Poles, Corroded Crossarms, Rotten Shells, Broken Ground Lead Wires, and Buildings Encroachment in Right Of Way * Structures loading does not meet current NESC standards.
AEP-2019-AP025 | AEP | PJM West | 2019-07-24 | 2020-10-16 |  |  |  | Floyd County, Kentucky | * The existing Allen station has historically experienced severe flooding due to the stations current location in the flood plain. Historical flooding issues have lead to significant deterioration of the stations foundations and structures. * The 46 kV Circuit Breakers (CBs) A, B, C, & D are oil filled breakers without oil containment manufactured in 1960s. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. These units comprise 4 of the remaining 12 of the FZO-69-1500P model family on the AEP System. Spare parts for these units are difficult to impossible to procure, and this model type is no longer vendor supported. * The circuit breakers have experienced the following fault operations, CB A (27), C (20), and D (17). The manufacturer recommendation is 10 fault operations during it’s in-service life. In addition, all CBs have documented malfunction records with A, C, and D having at least 1 documented since 2016. These include mainly air leaks, a broken trip latch component, and a trip test switch malfunction. The platform foundations that these are mounted on are crumbling in several locations. * The 46 kV CS AA is a VBM-69 model type, 1 of 15 remaining on the AEP System. Spare parts for these units are difficult to impossible to procure, and this model type is no longer vendor supported. These circuit switcher models are poor cold weather performers. This unit has 8 documented malfunction records including multiple failures to trip on poles 2 and 3 and one instance in 2011 in which the unit failed to close.
AEP-2019-AP026 | AEP | PJM West | 2019-07-24 | 2020-01-17 | 2020-01-29 | S2177 |  | Fayette County, WV | Carbondale – Kincaid 46 kV #1 (~14.8 miles) * Majority of the circuit is constructed with 1950s wood and lattice structures * The conductor is greater than 65 years old. Grounding on this line does not meet current standards. * Between 2015-2018 the circuit experienced 16 momentary and 6 permanent outage resulting in approximately 140k customer minutes of interruption Carbondale – Kincaid 46 kV #2 (~18.6 miles) * Majority of the circuit is constructed with 1950s wood and lattice structures * The conductor is greater than 65 years old. Grounding on this line does not meet current standards. * From 2015-2018 the circuit has experienced 16 momentary and 7 permanent outages resulting in approximately 390k customer minutes of interruption. Carbondale 138/69/46 kV Station – 46 kV and 69 kV CBs A, B, C, D, F and G are all 1968, CF-48-69-2500 type breakers. * Spare parts for these units are difficult to impossible to obtain, and this model type is no longer vendor supported * These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling * These breakers have each exceeded the designed number of full fault operations (10). CB-A: 154, CB-B: 49, CB-C: 78, CB-D: 75, CB-F: 94, CB-G: 100 – Carbondale 138/69/46 kV transformer TR-1, manufactured in 1972, has experienced a sharp increase in combustible gas concentrations in January 2016. * Numerous gasses have remained at elevated levels, including acetylene at IEEE Condition 4 and ethylene at IEEE Condition 2. * The concentrations present are strongly correlated to electrical discharges of high energy and thermal faults in excess of 700° C. * Despite declining moisture levels and improving interfacial tension, oil power factor levels are on the rise, and dielectric strength is declining. This supports contamination in the oil from the high energy discharges and thermal faults. – The current MOAB/Ground SW configuration on TR-1 creates a fault in the station to signal the remote end breakers to open; this is a known safety hazard in legacy station designs. – The 138 kV line section towards Kanawha River terminates directly into the bus which creates a lack of operational flexibility when switching for faults on the circuit. – Carbondale Substation currently deploys 64 relays, implemented to ensure the adequate protection and operation of the substation. * 36 of the 64 relays (56% of all station relays) are in need of replacement. * 36 of the electromechanical which have significant limitations with regards to fault data collection and retention. Spare parts for these relays are difficult to obtain. Kincaid 138/69/46 kV Station – 46 kV CBs A, B, and J are all 1972 FK-72.5-27000-9 type breakers, accounting for 3 of 21 remaining of this model remaining on the AEP system. * Spare parts for these units are not available and this model type is no longer vendor supported * These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling * These breakers have each exceeded the designed number of full fault operations (10). CB-A: 61, CB-B: 123, CB-J: 72 – GND transformer PH 1-3 * All three single phase units of GND TR are experiencing similar health deterioration. * There are elevated levels of Acetylene at IEEE condition 2 and Carbon Dioxide at IEEE Condition 2 or 3. * The presence of excess acetylene may be a product of arcing causing overheating on this unit. High levels of carbon dioxide support this observation. * In addition, significantly diminished oil interfacial tension corroborates the frequent overheating events. Sludge has likely developed in the oil from particulate formation during arcing and other fault events. This sludge impairs the natural circulation of oil. * Moisture levels are on the rise which can lead to diminished dielectric strength over time. – The current 138 kV MOAB/Ground SW configuration on TR-1 creates a fault in the station to signal the remote end breakers to open; this is a known safety hazard in legacy station designs. – Kincaid Substation currently deploys 51 relays, implemented to ensure the adequate protection and operation of the substation. * Currently, 45 of the 51 relays (88% of all station relays) are in need of replacement. * There are 45 of the electromechanical which have significant limitations with regards to fault data collection and retention. Of these relays, 18 are in the top 90th percentile of relays on the AEP system targeted for replacement by PCE. * There appears to be little room in the existing control house to accommodate a relay replacement of this suggested magnitude. – The existing RTU installed at Kincaid is a GE D200MEII/Ethernet and has 2 documented malfunction records Boomer 46 kV Station – Customer no longer served from this station, no load at this station. Raynes 46 kV Station – Customer no longer served from this station, no load at this station. Alloy 46 kV Station Hard Tap – Hard taps are difficult to maintain due to required outages or temporary jumper configurations in lieu of a switch. – Hard taps can also result in extended outages to customers due to the inability to sectionalize faulted facilities.
AEP-2019-AP032 | AEP | PJM West | 2019-08-29 |  |  |  |  | Pike County, Kentucky | Equipment Material/Condition/Performance/Risk: The 46 kV transmission Cedar Creek – Elwood 46kV circuit (~15.5 miles) is 1966 Vintage and has 81 open conditions. The majority of open conditions are structure related including rot top/shell, woodpecker and burnt damage. The two permanent outages on this circuit have caused 176,728 CMI over the past five years. Also over this time span, there have been 18 momentary outages.
AEP-2019-AP033 | AEP | PJM West | 2019-09-25 |  |  |  |  | Buffalo, WV | Vandalia Growers has requested a new delivery point located near Buffalo, West Virginia. The projected peak load is 60 MVA.
AEP-2019-AP027 | AEP | PJM West | 2019-08-29 | 2020-03-19 | 2020-05-11 | S2225 |  | Hernshaw Area Project | Belle – Cabin Creek – Marmet Hydro 46 kV Circuit (7.58 miles) *Majority of the circuit is constructed with 1930s lattice structures. *Between 2015-2018 the circuit experienced 4 momentary and 3 permanent outage resulting in approximately 24 k customer minutes of interruption *There are currently 13 open conditions associated with the structures and hardware and include heavy rust, broken insulators and damaged shield wire hardware. *The line does not comply with current NESC Standards. *Most structures are situated on an extreme side hill, which also sits above the WV Turnpike which presents a significant danger/risk should the structures fail. *This line parallels the Belle – Cabin Creek – Marmet line, need AEP-2019-AP028.
AEP-2019-AP028 | AEP | PJM West | 2019-08-29 | 2020-03-19 | 2020-05-11 | S2225 |  | Hernshaw Area Project | Belle – Cabin Creek 46 kV Circuit (7.14 miles) *Majority of the circuit is constructed with 1930s lattice structures. *Between 2015-2018 the circuit experienced 6 momentary and 2 permanent outage resulting in approximately 242 k customer minutes of interruption *There are currently 13 open conditions associated with the structures and hardware and include heavy rust, broken insulators and corroded shield wire. *The line does not comply with current NESC Standards *Most structures are situated on an extreme side hill, which also sits above the WV Turnpike which presents a significant danger/risk should the structures fail. *This line parallels the Belle – Cabin Creek – Marmet line, need AEP-2019-AP027.
AEP-2019-AP029 | AEP | PJM West | 2019-08-29 | 2020-03-19 | 2020-05-11 | S2225 |  | Hernshaw Area Project | Marmet Hydro is currently served off a hard tap on the Belle – Marmet Hydro – Cabin Creek 46 kV circuit *Hard taps are difficult to maintain due to required outages or temporary jumper configurations in lieu of a switch. *Hard taps result in extended outages to customers due to the inability to sectionalize faulted facilities.
AEP-2019-AP034 | AEP | PJM West | 2019-09-25 | 2020-01-17 | 2020-01-29 | S2178 |  | Grayson County, VA | The Amos - Sisson 138 kV line is a 16 mile long radial line and maintenance cannot be performed due to length of outages required. Approximately 18 MVA is served out of Lanham and 25 MVA is served out of Sisson during winter peak conditions and will be dropped for outages on this circuit. Customers served out of the area are concerned and are requesting that we take necessary steps to ensure reliability.
AEP-2019-AP035 | AEP | PJM West | 2019-09-25 | 2020-01-17 | 2020-01-29 | S2178 |  | Kenna, WV | APCO Distribution has requested a new distribution station located in Kenna, West Virginia. Winter projected load 18 MVA.
AEP-2019-AP036 | AEP | PJM West | 2019-09-25 | 2020-01-17 | 2020-01-29 | S2179 |  | Patrick County, VA Area | The Floyd-Stuart 69 kV circuit (21.0 mi.) was originally built in 1939 consisting of wood pole structures and predominately 4/0 ACSR 4/1 overhead conductor. 88% of the wood poles are 1939 vintage. Core drilling shows significant loss of material in wood poles due to decay and woodpeckers. The overhead conductor and shield wires are greater than 65 years old, exceeding the recommended lifespan of these components. Between January 2014 and March 2019, 9 momentary and 2 permanent outages have occurred on this circuit. There are 52 open conditions mainly from woodpecker and wood rot.
AEP-2019-AP037 | AEP | PJM West | 2019-09-25 | 2020-01-17 | 2020-01-29 | S2179 |  | Patrick County, VA Area | Willis Gap station is served via a radial 14.5 mile, 138 kV line from Huffman Station and serves approximately 25 MVA of peak load. AEP is unable to take any outages of this circuit to perform necessary maintenance. Customers served in the area are concerned and are requesting that we take necessary steps to ensure reliability.
AEP-2019-AP038 | AEP | PJM West | 2019-09-25 | 2020-01-17 | 2020-01-29 | S2179 |  | Patrick County, VA Area | Distribution has requested the need for a new Claudville Station located between the existing Willis Gap and Stuart stations in order to decrease the exposure to lengthy 34.5 kV distribution circuits fed from Willis Gap and Stuart stations. A new distribution station source will allow for the opportunity to establish two new 34.5 kV feeders by splitting up the Willis Gap/Ararat (174 line miles) and the Stuart/Carroll (267 line miles) distribution feeders. The Willis Gap 138/34.5 kV #1 distribution transformer is projected to be loaded to 28.4 MVA, or 101% of its 28.0 MVA capability by winter 2022-23.
AEP-2019-AP041 | AEP | PJM West | 2019-10-25 | 2019-12-18 | 2020-01-29 | S2151 |  | Sullivan County, Tennessee | Eastman Chemical in coordination with Air Products, has requested a new point of service for their planned new facilities at Moreland Drive. The projected peak demand is 47 MW.
AEP-2019-AP046 | AEP | PJM West | 2019-11-22 |  |  |  |  | Pittsylvania County, VA | A siting assessment has been requested for establishing a new distribution station in anticipation of a future industrial customer(s) located at the Southern Virginia Mega Site at Berry Hill.
AEP-2019-AP042 | AEP | PJM West | 2019-11-22 | 2020-11-20 |  |  |  | Kincaid Area Project | Kincaid - Tower 117 69 kV (22.42 mile), includes Kincaid - Scarbro 46 kV line (10.1 miles) * The double circuit segment from Kincaid to Scarbro is comprised of a combination of lattice steel and wood poles. - Lattice structures utilize direct embed grillage foundation - Line originally installed in 1913, primarily with 3/0 Copper conductor - The structures failed to meet 2017 NESC 250B and 250D loading criteria - The lattice towers show flaking of the galvanized coating with significant section loss and corrosion above and below grade on the tower legs. - 4-bell insulators have noticeable wear and tear including rusting - The original conductor has visible signs of wear, such as burns and rust. * Since 2014 there have been 86 momentary and 27 permanent outages on the Kincaid - Tower 117 69 kV and Kincaid - Scarbro 46 kV circuits. - Majority of the momentary outages were due to weather including wind/lightning * This is indicative of insufficient shielding, and/or insufficient grounding - Permanent outages were caused by a vegetation fall-ins due to insufficient ROW and line equipment failures * These permanent outages attributed to 1.1M customer minutes of interruption * There are currently 33 structures with at least one open structural condition, which relates to 29% of the structures on the double circuit segment (10.1 miles). * There are currently 68 open structural conditions mainly related to heavy rust on lattice steel lacing and rot on poles/crossarms.
AEP-2019-AP048 | AEP | PJM West | 2019-11-22 |  |  |  |  | Sullivan County, Tennessee | * Reedy Creek CB A is a 32 year old GCB and it's the only breaker of its kind left on AEP system-there are no longer usable, retired breakers to harvest for spare parts. * It has 16 malfunction records related to SF6 leaks and 13 fault operations, exceeding the 10 operations recommended by manufacturer. * Units of similar design demonstrated serious issues relating to the accelerated deterioration of the rubber lines that comprise the hydraulic system. Losing pressure in the hydraulic system is an imminent failure mode and once detected, this failure mode can only be resolved by de-energizing the unit.
AEP-2019-AP049 | AEP | PJM West | 2019-11-22 |  |  |  |  | Beckley, WV | Bradley - Scarbro 46 kV Circuit * Majority of the circuit constructed utilizing 1913 wood and lattice structures * From 2015-2018 the circuit experienced a total of 8 momentary and 8 permanent outages resulting in a total of 665k customer minutes of interruption * There are currently 21 open conditions on 22% of the circuit * Conditions include heavy rust, woodpecker damage and broken conductor strands
AEP-2019-AP043 | AEP | PJM West | 2019-11-22 | 2020-02-21 | 2020-04-10 | S2190 |  | Henry County, VA | Fieldale-Dan River 138 kV Line Asset (14.8 mi.) Fieldale-Ridgeway 138 kV Circuit (10.3 mi.) 1949 wood H-Frame construction 58 Type A open conditions on 35 unique structures (51% of all structures on circuit) From 2015-2018, a total of 4 permanent outages resulting in 241,094 customer minutes of interruption Ridgeway-Dan River 138 kV Circuit (4.5 mi.) 1949 wood H-Frame construction 40 Type A open conditions on 23 unique structures (68% of all structures on circuit (owned by AEP)) From 2015-2018, a total of 3 permanent outages occurred
AEP-2019-IM010 | AEP | PJM West | 2019-04-23 |  |  |  |  | Dowagiac, Michigan Area | Colby Station * Breakers A, B, C, D, and E * 1963-1968 vintage oil breakers * CB Fault operations: CB A(38), C(67), D(86), E(12) – Recommended(10) * Breaker B control cabinet has documented corrosion concerns * Since 2017 breaker D's operation counter hasn’t functioned * Currently contains a 3-terminal line within the station.
AEP-2019-AP045 | AEP | PJM West | 2019-11-22 | 2020-02-21 | 2020-04-10 | S2191 |  | Henry County, VA | Henry County VA has requested a new delivery point in its Commonwealth Crossing Business Centre (CCBC) to initially serve Press Glass (5 MVA). The CCBC is located roughly 5 miles from the Sheffield-Ridgeway 138kV line in Ridgeway VA.
AEP-2019-AP047 | AEP | PJM West | 2020-01-17 | 2020-06-19 | 2020-09-15 | s2281 |  | Martin County, Kentucky | The 138/69/13.09 kV transformer TR1 is 1967 vintage and has seen significant increases in moisture levels and power factor which indicate a rise in concentrations of harmful particles within the oil. The Short Circuit strength is decreased due to the age of this unit's insulation materials. As the insulating paper ages, it becomes brittle allowing for increased susceptibility to short circuit faults causing failure of the main tank. The transformer has numerous observed oil leaks including fluid leaking from the internal wiring. The four 138 kV circuit breakers, B, B2, C and C1, are 1990's vintage SF6, type breakers. The circuit breakers have experienced the following fault operations: CB B (38), B2 (22), C (99), and C1(70). CB-B had 52 leaks reported in malfunction records related to low SF6 gas levels. CB-B2 had 24 and CB-C1 had 10 reported SF6 leaks. Inez Substation currently deploys 105 relays to ensure the adequate protection and operation of the substation. Currently, 71 of the 105 relays (68% of all station relays) are in need of replacement due to obsoleteness. 61 are of electromechanical type, six are static type, and four are disontinued microprocessor relays.
AEP-2019-AP050 | AEP | PJM West | 2019-11-22 | 2020-02-21 | 2020-04-10 | S2192 |  | Lynchburg, VA | Reusens-Altavista 138 kV Line Asset (11.6 mi.) A total of 16 open conditions on 13 unique structures (comprising 18% of the line asset) New London-Reusens 138 kV Circuit: From 2015-2018, a total of 2 permanent and 2 momentary outages occurred McConville-Reusens 138 kV Circuit: From 2015-2018, a total of 2 permanent and 2 momentary outages occurred 138 kV Double Circuit Section (5.5 mi.) 1949 steel lattice structures Structure loading does not comply with the NESC 250B and 250D standards for the line. The current shielding does not comply with the current standards, specifying a maximum of 30 degrees. The current shielding angle is approximately 50 degrees. 138 kV Single Circuit Section (6.1 mi.) 1949 wood H-Frame construction Structure loading does not comply with the NESC 250B and 250D standards for the line. The current shielding does not comply with the current standards, specifying a maximum of 30 degrees. The current shielding angle is approximately 50 degrees.
AEP-2019-IM012 | AEP | PJM West | 2019-04-23 | 2020-02-21 | 2020-04-10 | S2193 |  | Ft. Wayne, Indiana | Illinois Road 138 kV station * Breakers A & B 69 kV * 1969 and 1970 vintage Oil breakers * Fault Operations: A(23) & B(67) – Recommended(10) *Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported
AEP-2019-IM017 | AEP | PJM West | 2019-04-23 |  |  |  |  | Ft. Wayne, Indiana | Industrial Park – Wallen 34 kV (~3.3 Miles) * 1925 vintage steel lattice construction * There are currently 5 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. * Six wired Copper conductor with copper weld shield wire. Copper conductors become brittle with age and Copper weld conductor has long been obsolete * Industrial Park 138 kV * Breakers F, D & E 34 kV * 1967 vintage Oil breakers * Fault Operations: F(18), D(0) & E(14) – Recommended(10) * Breakers G 69 kV * 1967 vintage Oil breakers * Fault Operations: G(50) – Recommended(10) * Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported. * Multiple wood pole 138 kV transformer lead support structures inside Industrial Park Station.
AEP-2019-IM014 | AEP | PJM West | 2019-04-23 | 2020-09-11 | 2021-01-13 | s2393.1-.5 |  | Rob Park – S. Hicksville 69kV line rebuild | Robison Park – South Hicksville 69kV Line (~27 Miles) 1967 vintage wood cross arm construction. There are currently 56 open conditions on this line with majority (94%) being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. 4/0 ASCR conductor with horizontal post type porcelain insulators. CMI: 526,269 Forced Momentary Outages: 6 Forced Permanent Outages: 5 St Joe Tap 69kV Line (~0.6 Miles) 1967 vintage wood cross arm construction There are currently 3 open conditions on this line. The O&M cost of the line is expected to increase as the age of the line increases. St. Joe is radially served out of Robison Park – South Hicksville 69kV Line and it is susceptible to single event outages. It occasional encounter floodwaters of Bear Creek that leave some of the existing poles inaccessible. St. Joe Tap Switch The Switch has accessibility challenges due to St. Joseph River floodwaters.
AEP-2019-IM015 | AEP | PJM West | 2019-04-23 | 2020-11-20 |  |  |  | Bixler Area Improvements | The loads at Bixler and North Kendallville are 20.58 MW and 17.13 MW respectively. Bixler is radially served from a 2.89 mile long 138 kV line. North Kendallville is radially served from a 1.79 mile long 69 kV line.* Kendallville – North Kendallville 69 kV Line (~1.7 Miles) * 1960’s vintage wood pole construction * There are currently 5 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. * CMI: 1,541,297 * Forced Momentary Outages: 1 * Forced Permanent Outages: 9
AEP-2019-IM020 | AEP | PJM West | 2019-11-22 |  |  |  |  | Western Ft. Wayne, Indiana Area | Gateway 69/34.5kV Station 34.5kV CB C. 1952 FK Oil breaker Fault Ops: C(10) - Recommended:10 69/34kV XFR 1 1975 unit with IEEE level 4 CO2 and level 2 CO Documented leaks and insulating paper deterioration Columbia 138/69/34.5kV Station 69 CB's K. 1985 FK Oil breaker Fault Ops: K(22) - Recommended:10 34.5kV CB B 1951 FK Oil breaker Fault Ops: B(20)- Recommended:10 Whitley 34.5kV Station 34.5kV CB D & B. 1954 & 1963 FK Oil breaker Fault Ops: D(20) B(69) - Recommended:10 Gateway - Columbia 69kV line 1964 Wood crossarm style line with 13 open conditions across its ~2.5 miles Richland - Columbia 69kV line 1959 Wood crossarm style line with 29 open conditions across its ~13 miles. Churubusco - Whitley 34.5kV line 1946 Wood crossarm style line with 31 open conditions across its ~10.6 miles Columbia - Whitley 34.5kV line 1954 Wood crossarm style line with 2 open conditions across its ~3.4 miles Churubusco - Wallen 34.5kV line 1972 Wood crossarm style line with 42 open conditions across its ~11.4 miles Carroll - Union REMC 34.5kV line 1968 Wood pole style line with 3 open conditions across its ~3 miles Carroll - Eel River 34.5kV line 1964 Wood pole style line with 1 open conditions across its ~3 miles Gateway - Columbia #1 Due to the load on this line, it's exposure, and the outages it has sustained in the last 10 years, this line requires additional sectionalization.
AEP-2019-IM022 | AEP | PJM West | 2019-06-17 | [5 empty] | Mount Etna 69kV Tap (~6.8 Miles) 1959 wood pole construction 5 open conditions 116 active maintenance events in the past 10 years Structures on this line fail to meet the current NESC loading requirements 7 permanent and 14 momentary outages in the 3 year timeframe between 2015-2018 641,081 CMI Radial lines are difficult to maintain without significant impacts to the customer
AEP-2019-IM016 | AEP | PJM West | 2019-04-23 | 2020-11-20 |  |  |  | Eastern Melita Area Improvements | Anthony – Harvest Park No.2 34kV Line (~2.5 Miles) • 1930’s vintage wood crossarm construction • There are currently 14 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. Anthony 34kV station • Breakers H, Q, D, C & A 34kV • 1970 vintage FK Oil breakers • Fault Operations: H(21), A(12) – Recommended(10) • Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported Harvest Park 34kV station • Breakers S, N, A & B 34kV • 1962 vintage FK Oil breakers S, N & B • 1956 vintage FK Oil breakers B • Fault Operations: A(49) – Recommended(10) • Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported
AEP-2019-IM018 | AEP | PJM West | 2019-11-22 | 2019-12-18 | 2020-01-29 | S2152 |  | Ft. Wayne, Indiana | 1. McKinley - General Electric Taylor West 34kV Line (~0.9 Miles) 1956 vintage wood pole, crossarm construction There are currently 9 open conditions on this line. Open conditions include: Damaged and rotted structures, stolen ground lead wires and broken knee/vee brace. 2. McKinley - Slater Steel 34kV Line (~0.98 Miles) 1967 vintage wood pole, crossarm construction There are currently 4 open conditions on this line. Open conditions include: Broken, missing, or stolen ground lead wires. 1. Bass - McKinley 34.5kV (~3.5 Miles) 1930 vintage steel single circuit lattice construction. There are currently 4 open conditions on this line. Six wired Copper conductor with copper weld shield wire. Copper conductors become brittle with age and Copper weld conductor has long been obsolete McKinley 138/69/34.5kV station Breakers F,J,K & M 34kV 1956 vintage FK Oil breakers which have been known to fail violently. Breaker DD 34kV 1962 vintage FK Oil breakers which have been known to fail violently. Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported Slater Steel 34kV station Customer-owned 34 kV switching facilities inside Slater Steel Station. Concerns about employees safety while switching in the customer station
AEP-2019-IM019 | AEP | PJM West | 2019-06-17 | 2020-02-21 | 2020-04-10 | S2194 |  |  | Adams 138/69kV station The 138/69kV XFR currently is protected by a high side ground switching MOAB. Currently there are 3 dissimilar zones of protection at this station with a 138kV line, 138kV bus and a 138/69kV transformer Pennville 138kV station This station’s through path is composed of wood support structures and cap and pin bus insulators, both have been identified as safety concerns. The Cap and Pin support insulators have a documented history of failing due to degradation in the glue that holds them together. It is currently AEP policy to remove these support style insulators whenever we come across them. The support structures for the station’s through path reside mostly outside of the station footprint. These bus support structures straddle the station fence which leaves most of the main bus, switches, insulators and support structures outside the station’s footprint where there is no ground grid. This has been identified as a safety hazard and will be addressed.
AEP-2019-IM024 | AEP | PJM West | 2019-06-17 | 2019-11-22 | 2020-01-29 | S2146 |  | Delaware - Kenmore 34.5 kV Rebuild | Delaware – Bethel overhead 34.5kV Line (2.8 miles) 1960’s vintage wood construction. 16 open conditions all related to structural issues. Issues with ROW encroachments. Bethel – Kenmore underground 34.5kV line (.8 miles) 1960’s vintage underground construction. Both cables are through common man-hole ducts, which can present a safety issue. Currently TFS personal will not work on this line unless both northern feeds to Kenmore are de-energized due to this configuration. Underground construction makes it difficult to identify and fix outages. This means that as this cable ages, the area will start experiencing prolonged forced outages. This line has already experienced multiple of these type of outages. This UG section was out for 14 straight days in June 2010 and 29 straight days in August 2017
AEP-2019-IM031 | AEP | PJM West | 2019-02-20 | [5 empty] | Portland 69kV station Breakers “A” and “G” 1962-1969 vintage Oil breakers Fault Operations: A(57) G(89) – Recommended(10) Trinity Tap (Jay REMC/Wabash Valley Power Authority) Potential economic developments have not materialized due to system load limitations. WVPA is targeting this area for load growth.
AEP-2019-IM025 | AEP | PJM West | 2019-10-25 | 2019-12-18 | 2020-01-29 | S2167 |  | Pokagon – Lake Street 69kV line | Pokagon – Lake Street 69kV line (4.9 miles) 28 open conditions 1952 wood cross-arm construction Many weather related failures/outages 12 momentary outages over the last 10 years
AEP-2019-IM027 | AEP | PJM West | 2019-08-29 | 2020-02-21 | 2020-04-10 | S2194 |  |  | Adams 69 kV Station: 69 kV Circuit Breaker D Vintage 1966 Oil filled McGraw Edison CF type breaker Last oil breaker at Adams station Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require Spare parts are not available and these models are no longer vendor supported Fault operations (10) – Manufacturers recommended maximum (10)
AEP-2019-IM037 | AEP | PJM West | 2019-02-20 |  |  |  |  | South Bend, Indiana Area | Torrington Tap 34kV Line (~1 mile): wood pole line, 2 open conditions. This trend is expected to increase as the structures and conductor age.
AEP-2019-IM030 | AEP | PJM West | 2019-02-20 | 2019-12-18 | 2020-01-29 | S2153 |  | Hillcrest - Adams 69 kV rebuild | Hillcrest – Bluffton 69kV line 1964 vintage wood pole line This line is currently subject to 155 open conditions with the majority being structural issues. This trend is expected to increase as the structures and conductor age. Adams – Bluffton 69kV line 1957 vintage wood pole line This line is currently subject to 32 open conditions with the majority being rotting structural issues. This trend is expected to increase as the structures and conductor age. Kingsland 69kV station Breakers “A” and “B” 1969 vintage Oil breaker Fault Operations: A(31) B(27) – Recommended(10) WVPA/Heartland Industrial Park 1 (Pleasant station) WVPA/Heartland has requested a new 138kV delivery point to feed a new industrial park. 2 industrial customers are already building on this site with room for further expansion. This load growth further constrains an already constrained 69kV network WVPA/Heartland Industrial Park 2 (Ossian station) WVPA/Heartland has target this area for industrial development. Potential economic developments have not materialized due to system load limitations. Kinnerk (WVPA/Heartland station) Customer has made an offer to upgrade this station to 138kV in order to enable to connect 138kV to the Pleasant and Ossian industrial parks. Kingsland (I&M Distribution) I&M Distribution has indicated a want to move toward 138kV at this facility due to the expected load growth in the industrial park north of this station.
AEP-2019-IM034 | AEP | PJM West | 2019-09-25 | 2020-02-21 | 2020-04-10 | S2195 |  | South Bend, Indiana | West Side 138 kV Station Three terminal line Three-terminal lines are very challenging to protect/coordinate and mis-operation or switching error become much more significant. Bus Tie Switch between the distribution transformers Bus Tie Switch when operated without de-energizing the whole bus jeopardizes the Bus Differential Protection. With no Bus Differential Protection the correct interrupting device wouldn't operate during fault scenarios, this can be dangerous for people working in the station.
AEP-2019-IM035 | AEP | PJM West | 2019-08-29 | 2019-12-18 | 2020-01-29 | S2167 |  | Niles Area Improvements | South Bend – Niles 69 kV Line (~11.47 Miles) *1968 vintage wood pole construction *Forced Momentary outages: 5 *Forced Permanent outages: 3 *Total structure related open conditions – 47 *Unique structure count with open conditions – 44 *Insect Damage, Rotten Poles, Broken/Burnt cross-arm, Woodpecker holes, broken/burnt insulators, stolen/broken ground wires, broken guy strain insulators and cracked stub pole. *More than three in-line sectionalizing MOABS
AEP-2019-IM038 | AEP | PJM West | 2019-10-25 | 2020-11-20 |  |  |  | Eastern Melita Area Improvements | Lincoln 138/69/34.5kV Station • I&M Distribution has requested a new delivery point at Lincoln station. • There is currently a three terminal line outside Lincoln station that connects Anthony, Lincoln and Robison Park. AEP has been addressing these three terminal lines when feasible.
AEP-2019-IM041 | AEP | PJM West | 2019-11-14 |  |  |  |  | Sullivan, Indiana | Sullivan 765/345kV Station 765kV CB A2 • The Sullivan CB A2 is an ELF-SL8-4 Type SF6 breaker. • As of September 2019 there are 9 of these breakers remaining in AEP’s system including CB A at this station which just recently failed under AEP2019-IM036. • Since 2002, there have been 16 documented issues with the 9 remaining breakers dealing primarily with compressor failures and failure to open/reclose.
AEP-2019-IM039 | AEP | PJM West | 2019-10-25 | 2020-02-21 | 2020-04-10 | S2196 |  | Customer Need-South Bend, IN | South Bend-Olive 138 kV line. New 1.5 MVA block load addition to the Ameriplex complex and new delivery point request from I&M distribution.
AEP-2019-IM040 | AEP | PJM West | 2019-10-25 | 2020-02-21 | 2020-04-10 | S2197 |  | Dragoon Station Needs | Dragoon Station: The 34.5 kV Circuit Breakers A, C and D at Dragoon Station are GE 'FK' oil-filled breaker manufactured in 1968 17, 51 and 9 fault operations (manufacturer recommendation of 10) Oil filled Breakers without oil containment The breakers have the following documented conditions: Bushing problems Unavailability of spare parts Fault operations count High moisture readings Oil spills are frequent with failures and routine maintenance which is also an environmental hazard
AEP-2019-IM045 | AEP | PJM West | 2019-11-22 |  |  |  |  | East Elkhart Customer Needs | Request from NIPSCO to serve 100MW of load located approximately 2-3 miles east of East Elkhart station
AEP-2019-IM041 | AEP | PJM West | 2019-11-14 | 2020-03-10 | 2020-05-11 | S2212 |  | Sullivan Station Improvements | Sullivan 765/345kV Station 765kV CB A2 The Sullivan CB A2 is an ELF-SL8-4 Type SF6 breaker. As of September 2019 there are 9 of these breakers remaining in AEP’s system including CB A at this station which just recently failed under AEP-2019-IM036. Since 2002, there have been 16 documented issues with the 9 remaining breakers dealing primarily with compressor failures and failure to open/reclose.
AEP-2019-IM047 | AEP | PJM West | 2020-01-17 |  |  |  |  | Niles, Michigan Area | Pletcher - Buchanan 69 kV line 1963 wood crossarm style line with 48 open conditions across its ~8.4 miles
AEP-2019-IM048 | AEP | PJM West | 4/23/2019, 11/20/2020 |  |  |  |  | Eastern Melita Area Improvements | Lincoln – Tillman 69kV Line (~13 Miles) • 1968 vintage wood crossarm construction • There are currently 24 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases.
AEP-2019-OH004 | AEP | PJM West | 2019-03-25 | [5 empty] | * Timken 138/23kV Station (vintage 1966) has many asset renewal issues, which is a concern, as the Station serves one of AEP’s largest industrial customers. * The 138/23 kV transformer #3 (vintage 1966) has had overheating events, insulating paper carbonization, and signs of gassing. * The 138/23 kV transformer #1 (vintage 1966) has dielectric strength breakdown from numerous through-fault events. * There are two oil-filled 138kV circuit breakers (A & B, GE ‘FK’ type, rated 1200A / 20.9kA) that actually pre-date the station (1953-vintage, as they were transferred from an older station). There are no oil-containment systems for the transformers or breakers. * The protection & control system is very antiquated, and comprises of 59 electromechanical relays, 1 static relay, and an obsolete RTU. EM relays have no spare part availability, lack vendor support, have no SCADA functionality, and lack fault data collection ability. The control house has no fenced boundary which is a security concern. * An outdated pilot wire scheme connects to the two 138kV remote-ends. * Timken is also space constrained making any improvements/modifications to the Station difficult. * Timken is a 3 breaker Station in a straight-bus configuration (2- 138kV sources, 4- 138-23kV transformers). This configuration has several instances of dissimilar zones of protection (bus, line, and transformer ) which can cause miss-operations and over tripping. In addition, a lack of sectionalizing makes maintenance a concern from an customer outage perspective.
AEP-2019-IM042 | AEP | PJM West | 2019-11-14 | 2020-06-02 | 2020-09-15 | s2280 |  | Rockport Station Improvements | Rockport 765kV Station 765kV CB’s A, B, B1, B2, C and C2 • These Rockport CB’s are ELF-SL8-4 Type SF6 breakers. • As of September 2019 there are 9 of these breakers remaining in AEP’s system including CB A at Sullivan station which just recently failed under AEP-2019-IM036. • Since 2002, there have been 16 documented issues with the 9 remaining breakers dealing primarily with compressor failures and failure to open/reclose.
AEP-2019-IM044 | AEP | PJM West | 2019-11-22 | 2020-08-14 | 2020-10-21 | s2351 |  | Twin Branch Hydro 34.5kV Solution | Twin Branch Hydro 34.5kV Station: 34.5kV Breakers: The 34.5 kV Circuit Breakers CB, BB, DD, HH, and NN at Twin Branch 34.5kV Station are GE 'FK' oil-filled breaker manufactured in the 1950's. Common failure modes documented in AEP malfunction records for these breaker types are: compressor failures and valve defects, which cause low pressure and oil leaks. trip or reclose failures, caused primarily by spring latching and charging motor component failures. the vacuum oil and oil breakers have a lot of oil contamination from aging gaskets allowing moisture and other particle ingress. Oil spills are frequent with failures and routine maintenance, which can also present an environmental hazard Because these breaker types are no longer manufactured, spare parts are not available. 34.5/4kV Transformer #4: The interfacial tension of the oil is below acceptable limits and the moisture content in the oil relates to a level of relative saturation. These indicate that: sludge has formed in the radiators, core and coil. high moisture levels in the oil and paper insulating materials. the transformer oil is in poor quality to withstand dielectric events. Due to the age of this transformer, oil processing is not feasible option to extend the life of the unit.
AEP-2019-IM046 | AEP | PJM West | 2019-11-22 | 2019-12-18 | 2020-01-29 | S2167 |  | Niles Area Load Increase | Lake Street 69/34.5kV station New load delivery point which will serve ~8MW. South Bend - Niles 69kV line New load delivery point which will serve ~15MW.
AEP-2019-OH007 | AEP | PJM West | 2019-03-25 | 2019-12-18 | 2020-01-29 | S2155 |  | Findlay, Ohio | Findlay Center Station: - 34.5 kV CB's A, B, C, and D are oil type breakers (vintage 1962). Many of these breakers have exceeded the manufacturers recommended number of fault operations (10): A "(37), "B "(7),"C" (6), and "D" (39). - 34.5 kV cap switcher AA is a MARK-V model (2004) which has been identified for replacement due to lack of spare parts, operational and reliability concerns, and maintenance issues. Findlay Station: - 34.5 kV CB's A, B, D, and E are oil type breakers (vintage 1953- 1955). Many of these breakers have exceeded the manufacturers recommended number of fault operations (10): "A"(20), "B" (33), "D" (41), and "E" (3). - 34.5 kV cap switcher AA is a VBM model (1988) which has been identified for replacement due to lack of spare parts, operational and reliability concerns, and maintenance issues. Plaza Street Station: - 34.5 kV CB A is an oil type breaker (vintage 1948). This breaker has exceeded the manufacturers recommended number of fault operations (10): "A" (13). East Findlay Station: - The three-way switch (1958) has ongoing difficulties maintaining proper alignment of switches. The insulators are cap-and-pin type which often physically failing during switching operations. **Oil breaker maintenance is difficult due to the oil handling requirements and there is a risk for oil spills during failures and maintenance. These breakers are FK model breakers that have historical reliability concerns and lack of spare part availability. Line: Findlay - Findlay Center Circuit (1934) * Length: 3.43 miles * Original Construction Type: Wood * Original Conductor Type: 4/0 Copper 7 * Total structure count: 98 * Number of open conditions: 49 - Open conditions include: damaged conductor, pole rot, insect damage, contaminated insulators * Unique structure count with open conditions: 37 * Additional Info: N/A "
AEP-2019-OH011 | AEP | PJM West | 2019-03-25 | 2020-04-20 | 2020-06-15 | S2248 |  | Apple Valley Switch | * The Apple Valley (Licking Co-op) 138 kV delivery point serves approximately 2,300 customers with a peak demand of 6.5 MW. Apple Valley isn’t 100% transferrable during all times of the year and can take several hours to complete the required switching. This delivery point has experienced 971,280 customer minutes of interruption. * This delivery point is connected with a hard tap which limits sectionalizing during outages and maintenance. In addition, relay coordination can be difficult with hard taps.
AEP-2019-OH012 | AEP | PJM West | 2019-03-25 | 2020-02-21 | 2020-04-10 | S2198 |  |  | * South Central Power is rebuilding Lockbourne 138kV Station due to asset renewal conditions. Lockbourne is currently radially served via AEP’s Harrison Station, this line is partially owned by AEP and South Central Power with the point of ownership change being Circleville. The current loading on this radial line is 65MW with plans for increased load. Total CMI 2.7M over 3 year period. (2015-2018). * Radial service restricts the ability to perform routine maintenance and can cause extended outages to customers. The maintenance of radial transmission lines often requires cost-prohibitive temporary facilities or other labor-intensive measures.
AEP-2019-OH014 | AEP | PJM West | 2019-04-23 | 2020-02-21 | 2020-04-10 | S2184 |  | Adams County, Ohio | * The existing 28.5 mile, 69 kV line section between Stuart (DP&L/Duke) and Seaman(AEP) was constructed in 1974 using wood pole structures with 636 ACSR conductor. There are 260 open A conditions distributed across the 170 structures on this line. * The Stuart-Seaman 69 kV circuit has experienced over 2.2 million customer minutes of interruption in the past three years: 753,716 for AEP and 1,517,618 for Adams Coop.
AEP-2019-OH016 | AEP | PJM West | 2019-04-23 | 2019-12-18 | 2020-01-29 | S2156 |  | Bucyrus, Ohio | The Bucyrus-Howard No.2 69 kV circuit was originally constructed in 1919 with wood structures and copper conductor (#1 CU and 3/0 CU). 84% of the line still utilizes the original 1919 copper conductor. Some structures have been replaced over the years; however, they have been like for like wood pole replacements. The circuit has had 38 forced operations in the last 11 years of which 7 have been permanent and resulted in 54 hours of down time. 2 out of the 7 outages have been caused by conductor failures, the most recent of which resulted in 188,000 CMI. There are currently 144 open conditions along the 23 mile long line.
AEP-2019-OH020 | AEP | PJM West | 2019-04-23 |  |  |  |  | Columbus, Ohio | * Equipment Material/Condition/Performance/Risk: * The 40 kV system is an obsolete voltage class and as a result is difficult to obtain replacement parts. * Wilson Road Station * 1 – 40 kV: CB-34 has 55 Fault Operations * 1 – 40 kV: CS-AA is an SF6 2030-69 model circuit switcher, which has been identified as needing replacement due lack of to spare part availability, historical reliability, and lack of vendor support. * 3 – 40 kV: (CBs 30,35, & 36) & 8 - 138 kV: (CBs 2-9) are oil type breakers. * 7-138 kV: (CBs 2-7) 1974 vintage FK oil breakers. * 2-138 kV: (CBs 8 & 9) 1967 & 1968 vintage GM oil breakers. * 138 kV CB-4 has 17 Fault Operations. * 195 – Electromechanical relays: EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. * Wilson Continued: * 13 – Microprocessor relays: The identified relays are obsolete, no longer supported, or have been identified as high risk of failures. * 4 – Static relay: this type of relay has significant limitations with regard to fault data collection and retention. * McComb Station * 5 – 46 kV: (CBs 41-45) oil type breakers * Fault Operations: (CB-42 = 15 & CB-43 = 26) * 1 – 138 kV CS-CC (Mark V): This model of switcher has been identified for replacement due to lack of spare part availability, historical reliability, and lack of vendor support. It also has 16 fault operations. * 117 – Electromechanical relays: EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. * McComb Station utilizes either ground switch/MOAB’s or MOAB’s for high side transformer protection. * Operational Flexibility and Efficiency: * There is currently a 3-terminal 138 kV hard tap between Wilson, Fisher Rd, and Hall Stations. 3-terminal lines are problematic because they limit sectionalizing and can cause mis-operations and over tripping. A single breaker failure will result in the loss of 5 transformers. * Customer Service: * AEP-Ohio plans to replace the Briggsdale 40 kV Station with a new Reaver 138 kV Station (s1606), which eaves Phillipi (customer owned station) on the local 40 kV system.
AEP-2019-OH017 | AEP | PJM West | 2019-04-23 | 2020-01-17 | 2020-01-29 | S2157 |  | Columbus, Ohio | AEP-Ohio is requesting a new 138 kV delivery point at Hayden Station by 6/1/2020. There are several highly loaded distribution circuits at Dublin, Davidson, & Hilliard Stations that require a new delivery point.
AEP-2019-OH018 | AEP | PJM West | 2019-04-23 | 2021-02-17 |  |  |  | Muskingum to Tuscarawas Counties, Ohio | The Philo-Newcomerstown 138kV transmission line section is 33 miles long, originally constructed in 1923. The vast majority of the structures are still original, as well as the six-wired 336 ACSR conductor, insulators, and hardware. This line is made up of several circuits connected between Muskingum River and Newcomerstown stations. Insulator assemblies are showing corrosion and deterioration, which could lead to additional failures and safety concerns. There have been 1.4 million customer-minutes-of-interruption (CMI) over the 2008-2018 time period. This line has experienced 8 momentary outages and 3 sustained outages over the past 10 years. The East New Concord Station is connected via a hard tap (no sectionalizing switches present). Lack of sectionalizing requires a substation outage whenever maintenance or emergency repairs are performed on either side of the 138kV tap.
AEP-2019-OH019 | AEP | PJM West | 2019-04-23 | 2019-11-22 | 2020-01-29 | S2147 |  | Belmont / Harrison County, Ohio | * The Glencoe – Robyville 69 kV circuit is 13.3 miles long and originally constructed in 1915-1925 using wood pole structures. This circuit currently has 556 ACSR 18/1 (Osprey) conductor rated for 126 MVA WE. * The Glencoe – Robyville 69 kV circuit has 136 open A conditions which includes broken shield/ground wires, heavy structure rot, woodpecker damage, broken insulators, and split cross arms/knee braces. * This circuit has experienced 789,612 CMI between 2013 – 2018. * The existing switch at Highland Terrace two-way GOAB that restricts our ability to perform routine maintenance and restoration activities in this remote area of our system. * The Shepherdstown delivery point is connected via a hard tap which limits operational flexibility, can cause over tripping and relay mis-operations, and restricts restoration activities.
AEP-2019-OH023 | AEP | PJM West | 2019-05-20 | 2019-12-18 | 2020-01-29 | S2158 |  | Beaver, OH | Equipment Material/Condition/Performance/Risk: The East Beaver - Buckeye Co-Op 69 kV line was built in 1952. 60 out of the 71 wood structures of this 4.5 mile line are of early 1950s vintage and are affected by heavy rot and woodpecker & insect damage. There are 26 open A conditions on this line. The conductor on the entire line has never been replaced since originally installed. Operational Flexibility and Efficiency Currently, the East Beaver 138/69 kV station has more than 2 dissimilar zones of protection (bus, line, and transformer).
AEP-2019-OH024 | AEP | PJM West | 2019-05-20 | 2020-02-21 | 2020-04-20 | S2201 |  |  | *The 1943 Hillsboro – Millbrook Park 138 kV circuit (~52 miles) is wood pole construction and has 1,342 open conditions. *The majority (93%) of the original conductor (vintage 1944 & 1948) is 477 MCM (26/7) ACSR and is still in-service. *Half of the wood pole structures from the 1940’s are still in-service; the remaining are a mixture from 1960’s – 1980’s. *There are additional concerns with the shielding, grounding, and hardware along this 52 mile long line. *Sinking Springs is in a remote part of AEP’s service territory making manual switching difficult.
AEP-2019-OH028 | AEP | PJM West | 2019-03-25 | [5 empty] | Coolville 69kV station is radially served on a 1954 vintage line (~12.6 miles) utilizing 4/0 ACSR 6/1 (Penguin) conductor (50/63 MVA SN/WN). This radial line has 84 structures, 22 of which have pole related open conditions and 28 of which have ground lead wire issues/concerns. It has experienced 4.4 million CMI over the last three years. Radial lines restricts the ability to perform routine maintenance and restoration activities.
AEP-2019-OH025 | AEP | PJM West | 2019-05-20 | 2020-05-22 | 2020-08-06 | S2272 |  | Millbrook Park-South Point Rebuild | *The South Point – Portsmouth 138 kV double circuit is 34.7 miles and the Bellefonte 138 kV Extension is 4 miles in length.*The conductor is primarily 397.5 ACSR (167 MVA).*The South Point-Portsmouth line was originally constructed in 1929, with the majority of the structures and conductor being original.*There are 45 open conditions on the line, including conductor issues, burnt/broken insulators, and loose/broken conductor hardware.*Insulators of this vintage have shown heightened failure rates.*In general, several issues impact 1920 lattice tower lines:*The steel conductor attachment plates have significant wear resulting in a loss of 50% of its strength.*The cross arm hanger tension members are single mode of failure elements that are deteriorated and undersized due to the original design criteria.*Lattice towers of this vintage do not meet current design requirements for wind and ice loading.*Foundations are undersized for modern wind loading.*Towers are beginning to show corrosion.
AEP-2019-OH031 | AEP | PJM West | 2019-06-17 | [5 empty] | Honey Creek SW - North Central Co-op Line Section (vintage 1955) Length: 8.06 Miles Original Construction Type: Wood Original Conductor Type: 1/0 ACSR 6/1 (Raven) Momentary/Permanent Outages: 13 in the past 5 years CMI: 2,505,168 Number of open conditions: 46 Open conditions include: Damaged HP Insulators, Poles, Ground Lead, & Guy Wires Additional Info: Radial service severely restricts the ability to perform routine maintenance and restoration activities. The maintenance of radial transmission lines often requires costly temporary facilities or other labor-intensive measures involving energized work because a maintenance outage to such radial loads is generally not feasible.
AEP-2019-OH032 | AEP | PJM West | 2019-06-17 | [5 empty] | West Rockaway – North Central Co-op Line (vintage 1960) Length: 8.32 Miles Original Construction Type: Wood Original Conductor Type: 1/0 ACSR 6/1 (Raven) Momentary/Permanent Outages: 13 in the past 5 years CMI: 2,505,168 Additional Info: Radial service severely restricts the ability to perform routine maintenance and restoration activities. The maintenance of radial transmission lines often requires costly temporary facilities or other labor-intensive measures involving energized work because a maintenance outage to such radial loads is generally not feasible.
AEP-2019-OH034 | AEP | PJM West | 2019-06-17 | [5 empty] | South Greenwich-Willard (vintage 1964) Length: 15.22 Miles Original Construction Type: Wood Original Conductor Type: 4/0 ACSR 6/1 (Penguin) Momentary/Permanent Outages: 13 in the past 5 years Number of open conditions: 77 Open conditions include: Damaged Insulator, Structure, Guy Wire, Ground Lead Wire, & Shield Wire Radial service severely restricts the ability to perform routine maintenance and restoration activities. The maintenance of radial transmission lines often requires costly temporary facilities or other labor-intensive measures involving energized work because a maintenance outage to such radial loads is generally not feasible.
AEP-2019-OH026 | AEP | PJM West | 2019-05-20 | 2019-12-18 | 2020-01-29 | S2159 |  | Gallia County | The 58-mile South Point - Sporn 138 kV double circuit line has four delivery points that are connected via hard taps. The hard taps complicate restoration activities and extend outages. The four Buckeye Coop delivery points are at Mercerville, Windsor, Fayette, and Addison. These stations are in a remote part of AEP's service territory, which makes outage restoration activities more difficult and resulting in longer outages. Over the last five years these delivery points have accumulated 1,348,755 CMI.
AEP-2019-OH027 | AEP | PJM West | 2019-05-20 | 2020-02-21 | 2020-04-10 | S2185 |  |  | *The majority (94%) of the Sunnyside-Torrey 138 kV line (4.3 miles) is comprised of steel lattice towers built in 1918, with the remaining 6%, dating back to 1954.*The conductor is original vintage (1918), consisting of 6-wired 200 MCM copper & 250 MCM copper.*Note that the 0.3-mile customer tap was built in 2007 and is in adequate condition.
AEP-2019-OH030 | AEP | PJM West | 2019-06-17 | 2019-12-18 | 2020-01-29 | S2160 |  | Crooksville - North Newark Rebuild | Line: Crooksville - North Newark (Vintage - 1952) * Length: 30.63 Miles * Original Construction Type: Wood * Original Conductor Type: 266,800 CM ACSR 26/7 (Partridge) * Momentary/Permanent Outages: 5 outages last 5 years * Number of open conditions: 338 - Open conditions include: Pole Rot, Insect/Bird Damage, Damaged Conductors, Ground Wires, & Guy Wires.
AEP-2019-OH035 | AEP | PJM West | 2019-06-17 | 2020-11-20 |  |  |  | Holmes County, Ohio | Holmes-Wayne Electric Cooperative customers are connected to the Trail and Alpine delivery points that are served from the Berlin – Sugarcreek Terminal and Beartown – Moreland Sw 69 kV circuits in eastern Holmes County. The Trail and Alpine delivery points have accumulated approximately 2.4 million minutes of CMI in the past five years. The Trail delivery point is served radial via a ~4.1 mile wood pole line out of Shiehill Road Switch. Maintenance on the line is difficult to coordinate as it requires outages to Trail station.
AEP-2019-OH037 | AEP | PJM West | 2019-06-17 | 2020-03-19 | 2020-05-11 | S2216 |  | Lamping - Woodsfield | The Cameron-Switzer 69kV circuit is 16.2 miles long and serves 3 wholesale customer stations (over 3,800 customers), with a combined peak load of 11 MW. The circuit is radially fed from AEP’s Switzer Station, making it difficult to perform proactive maintenance or restoration activities after an outage. The circuit is located in a remote part of AEP’s service territory and traverses very hilly and wooded terrain. The 69kV transmission line is of wood pole construction and was built in 1970. There are currently 121 open conditions on the circuit, with the majority being structure deficiencies (e.g., burnt insulators, insect damage, & cracked cross-braces). In addition, the City of Woodsfield is served via a 69kV hard tap, with no line sectionalizing switches present. South Central Power Co-op has reported 1.1 million customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH041 | AEP | PJM West | 2019-06-17 | [5 empty] | Springfield Radial 69 kV Line Maintenance of the 4.5-mile radial line is difficult to coordinate as it requires an outage to Carroll’s station. Carroll Electric Cooperative has reported approximately 204,000 customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH042 | AEP | PJM West | 2019-07-24 |  |  |  |  | Hocking, Ohio | East Logan – South Lancaster 69kV (vintage 1923) * Length: 16.43 Miles * Original Construction Type: Steel Lattice/Wood * Original Conductor Type: 2/0 Copper * Momentary/Permanent Outages: 43 total outages * CMI: 872,607 in the last 3 years * Number of open conditions: 40 – Open conditions include: Burnt/broken insulators, pole rot, insect damage, damaged conductor
AEP-2019-OH038 | AEP | PJM West | 2019-06-17 | 2020-03-19 | 2020-05-11 | S2217 |  | Columbus, OH | 138kV circuit breaker 105S at Hyatt station is showing signs of deterioration. This is an oil breaker installed in 1980. Oil breaker maintenance has become more difficult due to the oil handling required to maintain them. Oil spills are frequent with breaker failures and routine maintenance and can become an environmental hazard. This is the last remaining oil breaker at Hyatt. Transformer 1A has failed at Hyatt station and needs to be replaced. Transformer 1B is the same age (1973) and type, and Transmission Field Services has expressed similar concerns with 1B as they did with 1A (pre-failure), including dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). The existing configuration of Hyatt station includes both 345/138kV transformers in the same protection zone. The 345kV side of this zone is only energized from one bus such that a single bus outage would outage both transformers.
AEP-2019-OH039 | AEP | PJM West | 2019-06-17 | 2020-06-19 | 2020-09-15 | s2283 |  | Centerburg Area, Ohio | Lott Delivery Point (CEC): Buckeye Power, on behalf of Consolidated Electric Cooperative, has requested transmission service in Delaware County west of Centerburg, Ohio. Consolidated Electric Cooperative customers are currently connected to a radial 34.5 kV distribution line from AEP Ohio’s Trent station. The delivery point has consistently been identified as having poor reliability by Buckeye. Consolidated Electric Cooperative has reported approximately 700 thousand customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH045 | AEP | PJM West | 2019-07-24 |  |  |  |  | Washington County, Ohio | * Buckeye Power, on behalf of Washington Electric Cooperative, has requested transmission service in western Washington County, Ohio. * Washington Electric Cooperative customers are currently connected to radial 23 kV and 12 kV AEP Ohio distribution lines in the area. * The delivery points connected to the 23 kV system have consistently been identified as having poor reliability by Buckeye. * Washington Electric Cooperative has reported approximately 745 thousand customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH046 | AEP | PJM West | 2019-07-24 |  |  |  |  | Wayne County, Ohio | * Holmes-Wayne Co-op’s Moreland delivery point is served via a hard tap from the Beartown-Moreland 69kV circuit, with no line sectionalizing switches present. The hard tap limits operational capabilities in the area. It is difficult to coordinate maintenance efforts because the T-line cannot be removed from service without a customer outage for Holmes-Wayne Co-op. * Load is approximately 7 MVA. * CMI: .155 M reported by Holmes Wayne (2015-2018)
AEP-2019-OH040 | AEP | PJM West | 2019-06-17 | 2020-03-19 | 2020-05-11 | S2221 |  | Senecaville Loop 69kV | Derwent – Senecaville 69 kV circuit The Derwent – Senecaville 69 kV circuit is ~4.3 miles long and serves a AEP Ohio and Guernsey-Muskingum Electric Cooperative station radially out of Derwent station. Guernsey-Muskingum Electric Cooperative and AEP Ohio customers are currently served off the radial line. Maintenance on the line is difficult to coordinate as it requires outages to multiple stations. Guernsey-Muskingum Electric Cooperative has reported approximately 210,000 customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH049 | AEP | PJM West | 2019-09-25 |  |  |  |  | Ross County, Ohio | * South Central Power is requesting a new 69 kV delivery point at Paint Creek to alleviate several highly loaded distribution circuits out of SCP's Anderson & Budd Co. stations. * Peak load:12MW (Winter) * Requested ISD September 1, 2020
AEP-2019-OH043 | AEP | PJM West | 2019-07-24 | 2020-02-21 | 2020-04-10 | S2186 |  | Newark, Ohio | North Newark – Sharp Road 138 kV (vintage 1951) * Length: 19.38 Miles * Original Construction Type: Wood Pole * Original Conductor Type: 477 kcmil Hawk * Number of open conditions: 68 – Open conditions include: Burnt insulators, insect damage, pole rot, woodpecker damage
AEP-2019-OH044 | AEP | PJM West | 2019-07-24 | 2020-03-19 | 2020-05-11 | S2222 |  | Service to Ilesboro (65-91) 138kV | * South Central Power is requesting a new 138 kV delivery point on the Lemaster – Ross 138 kV circuit by September 2020. Anticipated load is about 4 MW.
AEP-2019-OH052 | AEP | PJM West | 2019-09-25 |  |  |  |  | Wood County, Ohio | North Baltimore - Portage 34.5 kV (1921) * Length:10.00 Miles * Original Construction Type: Wood * Conductor Types: 1/0 ACSR 6/1 (40%), 4/0 ACSR 6/1 (20%), 4/0 Copper 7 (30%), & 556,500 CM (10%) * Momentary/Permanent Outages: 11 (last 5 years) * CMI: 26,572 (AEP only) * Total structure count: 325 * Number of open conditions: 24 A" Conditions & 53 "B" Conditions - Open conditions include: (Damaged Insulators, Broken Shield Wires, Pole Rot, & Cracked Guys.) * Unique structure count with open conditions: 55 Additional Info: Portage is radially fed from AEP's North Baltimore station, Radial service severely restricts the ability to perform routine maintenance and restoration activities. The maintenance of radial transmission lines often requires costly temporary facilities or other labor-intensive measures involving energized work because a maintenance outage to such radial loads is generally not feasible. "
AEP-2019-OH047 | AEP | PJM West | 2019-07-24 | 2020-03-19 | 2020-05-11 | S2221 |  | Senecaville Loop 69kV | Derwent – Summerfield 69 kV * Majority of 13.8 mile circuit utilizes wood structures installed in 1962. * Circuit utilizes 336.4 kcmil ACSR 30/7 Oriole conductor installed in 1962. * Five momentary and permanent outages over last three years. * 62 Open Structure/Conductor conditions * Insect damage, woodpecker holes, along with rotted and cracked structures.
AEP-2019-OH049 | AEP | PJM West | 2019-09-25 | 2020-12-18 |  |  |  | Towhee Switch | South Central Power is requesting a new 69 kV delivery point at Paint Creek to alleviate several highly loaded distribution circuits out of SCP’s Anderson & Budd Co. stations. Peak load:12MW (Winter) Requested ISD September 1, 2020
AEP-2019-OH050 | AEP | PJM West | 2019-08-29 | 2020-03-19 | 2020-05-11 | S2218 |  | Bladensburg | *The Bladensburg Licking Rural Electrification Co-op (LRE) 138 kV delivery point, connected to the 45 mile North Bellville – Ohio Central 138 kV circuit, has a load of 3.9 MW peak demand serving 1449 customers. The Bladensburg load is 100% transferrable but under high loading conditions transferring loads can take several hours. For heavy loading periods LRE has experienced areas of low voltage while transferring loads. *The Blandensburg delivery point has experienced approximately 553,000 minutes of CMI over the last 5 years. *This delivery point is connected to the North Belleville – Ohio Central 138 kV circuit via a hard tap which limits operational flexibility and the effectiveness of protection schemes. In addition, it is difficult to coordinate maintenance efforts because the line cannot be removed from service without either a customer outage or temporary jumper configuration.
AEP-2019-OH051 | AEP | PJM West | 2019-09-25 | 2020-02-21 | 2020-04-10 | S2187 |  | Zanesville, OH | Customer Service: * Peak load: 30MW * A customer has requested new service on the Ohio Central - Philo #1 138 kV circuit.
AEP-2019-OH054 | AEP | PJM West | 2019-09-25 | 2019-12-18 | 2020-01-29 | S2155 |  | Findlay, Ohio | Findlay - Findlay Center Circuit (1934) * Length: 3.43 miles * Original Construction Type: Wood * Original Conductor Type: 4/0 Copper 7 * Total structure count: 98 * Number of open conditions: 49 - Open conditions include: damaged conductor, pole rot, insect damage, contaminated insulators * Unique structure count with open conditions: 37 * Additional Info: N/A
AEP-2019-OH055 | AEP | PJM West | 2019-10-25 | 2019-11-22 | 2020-01-29 | S2148 |  | South Canton, Ohio | 138 kV Circuit Breakers: K1, L1, & M1 * Interrupting Medium: SF6 * Additional Info: In addition to the 12 - 138kV overdutied breakers at South Canton, these remaining 3 breakers have fault duty in the 95-99% range.
AEP-2019-OH056 | AEP | PJM West | 2019-10-25 | 2019-12-18 | 2020-01-29 | S2161 |  | Columbus, Ohio | Huntley Station 69/12 kV Transformer #6 The 1976 vintage 69/12 kV transformer (33 MVA) has failed beyond repair in the field.
AEP-2019-OH065 | AEP | PJM West | 2019-11-22 |  |  |  |  | Delaware County, Ohio | Delaware 138 kV Station: Over the last five years Delaware station has accumulated approximately 2 million minutes of customer interruption associated with 19 outages at the station. 138 kV Circuit Breakers 104,106CB’s 104 and 106 are GM-5C type oil breakers. (1963, 1964 vintage) These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. Other drivers include damage to bushings, spare part availability, historical reliability, and lack of vendor support of the breakers. 138 kV Capacitor Switcher AA Mark V model which no longer supports modern relaying packages. Mark V’s have been historically prone to mechanism failures and are being replaced system wide where possible. 156/195 of the relays at this station are electromechanical and 12 are static type. These relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. In addition, there is corrosion on the steel structures, deteriorated/cracking foundations, existence of cap and pin insulators, and a non-standard station configuration.
AEP-2020-AEP001 | AEP | PJM West | 2020-12-01 |  |  |  |  | Ratings Methodology Changes | AEP is proposing to implement a ratings methodology change whereby single element open ratings would be applied to all facilities as part of their overall rating. This is to avoid any compliance violations of FAC-008 and TOP standards in case a breaker is opened. AEP’s historic practice was to apply a 2x multiplier to any facilities that connected in a configuration where flow could split between two paths in a station. This practice has been eliminated for any new facilities being constructed. AEP has maintained a list of facilities that continue to operate with a 2x multiplier on them pending future analysis and/or projects to address them. For the 2025 RTEP analysis, AEP worked with PJM to apply single multiplier ratings to all facilities on the system. There were four lines that were flagged in the 2025 analysis that show potential violations. Muskingum-Waterford 345 kV line. Jefferson-Clifty Creek 345 kV line. East Lima 345/138 kV transformer. Olive-New Carlisle 138 kV line (flagged in market efficiency analysis). AEP is proposing to address these needs in order to eliminate the exceptions and apply all single element open ratings in our future cases and in real time operations to comply with the request from PJM Operations and Planning. Once the flow enters the string, the flow is assumed to split 50/50 between the connected string elements. AEP’s historic practice was to apply a 2x multiplier for all elements in this portion of the branch definition (blue outline). When either breaker A1 or A is opened, the flow is forced through only one portion of the string. By changing the methodology, the ratings application will become consistent across all elements and branches. Because these are considered as part of a ratings methodology change, the future analysis was used to flag facilities where overloads may occur because of this change. AEP will propose supplemental projects to address the facilities of concern and will continue to apply the 2x multiplier exception until a project to replace the equipment driving the future overload is in service.
AEP-2020-AP001 | AEP | PJM West | 2020-01-17 | [5 empty] | Pax Branch – Toms Fork 46 kV line (~17.4 miles) • Majority of the circuit is constructed with wood structures varying in age from 49- 106 years old. The circuit also contains some lattice structures that are 50 years old. 85% of the line is constructed with 1950s wood. • 55% of the structures on the line have conditions • Steel structures show evidence of corrosion on arms and braces as well as hardware rusting • Wood structures show evidence of rot, split, and woodpecker damage. • The line is insulated with 4-bell porcelain insulators originally installed in 1915 and do not meet current AEP standards for CIFO and minimum leakage distance requirements • Approximately 70% of the line conductor is from 1915. • Static wire is 104 years old and does not comply with the current material standards. • Since 2014, the circuit experienced 8 momentary and 27 permanent outages.
AEP-2019-OH057 | AEP | PJM West | 2019-10-25 | 2019-12-18 | 2020-01-29 | S2162 |  | Hancock Co, OH | Buckeye Power, Inc. on behalf of Hancock Wood Electric, Inc. has requested a new delivery point adjacent to their existing site. AEP plans to relocate the existing switch to be able to serve the new delivery point.
AEP-2020-AP003 | AEP | PJM West | 2020-01-17 | [5 empty] | Station Name: Glen Lyn Circuit Breakers A, B, D, G, L & N (138 KV) Concerns: • All of these breakers are 63 years old, oil filled without oil containment; oil filled breakers pose significant environmental risk associated with oil handling and leaks. • Breakers A, B, D, L have experienced 55, 62, 11, 31 fault operations, respectively —exceeding manufacturer’s recommended number of 10. • Breakers A, B, D, G, and N are 5 of only 11 in the FGK-138-10000-3 model family remaining on the AEP system. • Breaker L is 1 of 4 in the FGK-138-10000-7Y model family remaining on the AEP system. AEP Transmission Zone: Supplemental Giles County, Virginia Kenna Glen Lyn SRRTEP-Western – AEP Supplemental 01/17/2020 6 Station (continued) Circuit Breakers AA, AC, AF (34 KV) Concerns: • All of these breakers are oil filled without oil containment; oil filled breakers pose significant environmental risk associated with oil handling and leaks. • CB AA is 71 years old, and is 1 of only 22 in the FK-339-1000 model family remaining on the AEP system. It has experienced 37 fault operations — exceeding manufacturer’s recommended number of 10. • CB AC is 42 years old, and is 1 of only 9 in the FK-439-34.5-1000-1 model family remaining on the AEP system. It has experienced 47 fault operations — exceeding manufacturer’s recommended number of 10. • CB AF is 71 years old, and is 1 of only 10 in the FK-339-1000-2 model family remaining on the AEP system. Circuit Switchers BB, CC, DD & P (138 KV) Concerns • CSs BB, CC, & DD are 40 years old. These circuit switchers belong to Mark V-138 model. There are numerous malfunction records on these units at Glen Lyn related to broken or malfunctioning operation counters. Failed operational components including high contact resistance, gas loss, and interrupter failure represent half of these malfunctions. Parts are expensive, especially because interrupters can only be replaced, not repaired, as they are hermetically sealed. • CS DD has experienced 55 fault operations —exceeding manufacturer’s recommended number of 10 during its in-service life. • CS P has experienced 235 fault operations —exceeding manufacturer’s recommended number of 10 during its in-service life. • There are a total of 5 malfunction records since 2002 for CS CC and DD relating (combined) to loss of SF6. AEP Transmission Zone: Supplemental Giles County, Virginia Kenna Glen Lyn SRRTEP-Western – AEP Supplemental 01/17/2020 7 Station (continued) Other station Specific equipment concerns: • Notable steel member corrosion existing on the 138 kV bay structures constructed in 1944. • All circuit breakers and circuit switchers foundations, along with station steel present concrete spalling and significant signs of deterioration beyond repair. • Lower elevation levels in the station yard are in the 100-year flood plain of the nearby New River. • No HVAC in 34.5 kV building reducing the life of digital equipment. Roof leaks in 34.5 kV building due to age and deterioration. 34.5 kV control house has only one entrance which does not meet current fire hazard protection standards. • Asbestos and lead paint in both of the control buildings. • The side of the fence has considerable corrosion and has an elevated risk of a slide occurring. • The current station access limits vehicle accessibility and is hazardous due to proximity to the neighboring railroad crossing. Accessibility constraints make repairs very difficult and increase outage time. Relay concerns: • Currently, 81 of the 115 are in need of replacement. There are 71 electromechanical and 10 static type relays which have significant limitations with regards to spare part availability and fault data collection and retention in addition to lack of vendor support. • There are 12 microprocessor based relays commissioned in from 1997 to 2008 with unsupported firmware. Two of the microprocessor relays have been previously identified to be replaced due to their elevated risk of failure in addition to obsolescence, lack of vendor support, and being out of warranty.
AEP-2020-AP004 | AEP | PJM West | 2020-01-17 | [5 empty] | Sullivan Gardens - Walters 138 KV (installed in 1927) • Length: 59.93 Miles • Original Construction Type: Lattice Steel • Original Conductor Type: 250,000 CM COPPER 12 • Momentary/Permanent Outages: 54/9 (5 years) • Total structure count: 448 • Number of open conditions: 91 – Open conditions include: burnt conductor, broken shield wire, broken hardware, structure rust. • Unique structure count with open conditions: 88 (20%) • Additional Info: N/A
AEP-2019-OH059 | AEP | PJM West | 2019-11-22 | 2020-03-19 | 2020-05-11 | S2215 |  | Putnam County, Ohio | Kalida - North Delphos (Original 1914) * Length: 11.26 * Original Construction Type: Wood * Original Conductor Type: 4/0 Copper 7 * Momentary/Permanent Outages: 9 Momentary, 3 Permanent (5 year) * CMI: 206,131 (5 year) * Total structure count: 268 * Number of open conditions: 58 - Open conditions include: rot heart, insect damage, broken/missing ground leads, burnt insulators * Unique structure count with open conditions: 50
AEP-2020-AP006 | AEP | PJM West | 2020-02-21 | [5 empty] | Ridgeway Station • 138/69 kV Transformer 2A • Manufactured in 1960 • Elevated levels of ethylene, CO2, and CO due to insulating paper breakdown. • The existing foundations for the transformer are wood tie foundations. Wood tie foundations cannot be patched or fixed like their concrete counterparts. • 138 kV Series Reactors #1, #2 and spare • Manufactured in 1944 • All of the Reactor 2 units are showing reduced interfacial tension levels in the oil, indicating the beginnings of sludge generation. There are leaks on Reactor 2 Phase 2. The dielectric strength of the oil in the spare unit has continued to decline. • Reactor 1 Phase 2 has declining dielectric strength and rising moisture content. The reactor bushings are subject to leakage. The foundations are built with wood ties with signs of rot. • The spare unit has low interfacial tension on the oil, indicating contaminates and sludge in the oil itself. If needed, this unit would have impaired circulation and cooling capability. • None of the reactors have oil containment. AEP Transmission Zone: Supplemental Henry County, VA SRRTEP-Western – AEP Supplemental 02/21/2020 Ridgeway 4 Continued from previous slide … • Ridgeway Station • 138/34.5 kV Transformer 1 • Manufactured in 1972 • Increased acetylene levels due to through faults and increased moisture levels due to gasket leaks and insulating paper breakdown. • 138 kV circuit switchers U and V • CS-U manufactured in 1979, CS-V manufactured in 1974 • MARK V-138 model types lack a gas monitor and have a history of malfunction. Both of these circuit switcher models have presented AEP with a large amount of failures and mis-operations. • Relaying • Currently, 41 of the 61 relays (67% of all station relays) are electromechanical type which have significant limitations with regards to spare part availability and fault data collection and retention in addition to a lack of vendor support.
AEP-2019-OH061 | AEP | PJM West | 2019-11-22 | 2019-12-18 | 2020-01-29 | S2163 |  | Dover 69 kV Service | * The City of Dover (municipal customer) has a normally-open 69 kV backup delivery point from AEP at South Intertie Switch. Dover is normally served by AEP from the North Intertie 138 kV station. Dover has requested that AEP close the normally-open 69 kV switch, to provide two parallel points of service. Dover's peak summer load is 45 MW.
AEP-2019-OH062 | AEP | PJM West | 2019-11-22 | 2019-12-18 | 2020-01-29 | S2164 |  | Delaware County, Ohio | Delaware 138 kV Station: Over the last five years Delaware station has accumulated approximately 2 million minutes of customer interruption associated with 19 outages at the station. 138 kV Circuit Breaker 114 CB 114 is an FK type oil breaker (1964 vintage) These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. Other drivers include damage to bushings, spare part availability, historical reliability, and lack of vendor support of the breakers.
AEP-2020-AP009 | AEP | PJM West | 2020-02-21 | [5 empty] | Elwood 46kV Station: 46 kV Circuit Breakers A,B, and C • 1960’s vintage FZO-69-1500P type oil circuit breakers. • Fault Ops: CB A (33), CB B (83), and CB C (105 ). Recommended : 10 • Other drivers: damage to bushings, spare part availability, historical reliability, and lack of vendor support of the breakers. • There are 8 remaining FZO-69-1500P circuit breakers on the AEP system, including the 3 at this station. • 86% of the relays (36/42) at the station are electromechanical, which have significant limitations with regards to fault data collection and retention and have no spare part availability due to a lack vendor support.
AEP-2020-AP010 | AEP | PJM West | 2020-03-10 |  |  |  |  | Axton, VA | The 765/138 kV phase 1 transformer at Axton failed. The on-site spare unit was switched in. There is currently no spare at site to deal with any future failures.
AEP-2020-AP011 | AEP | PJM West | 2020-02-21 | [5 empty] | Beaver Creek – Elwood 46kV: • Original Install Date: 1930s vintage • Length of Line: ~10.48 mi • Total structure count: 60 • Original Line Construction Type: Wood • Conductor Type: 336 ACSR • Momentary/Permanent Outages and Duration: 18 Momentary and 1 permanent Outage • CMI (last 5 years only): 269,070 minutes • Number of open conditions: 34 open conditions on 20 unique structures. • Open conditions include crossarms and poles with rot top, woodpecker damage and leaning-in-line conditions.
AEP-2020-AP012 | AEP | PJM West | 2020-02-21 | [5 empty] | Breaks– Dorton - Elwood 46kV: • Original Install Date: 1960s • Length of Line: ~26 mi • Total structure count: 135 • Original Line Construction Type: Wood • Conductor Type: 336 ACSR • Momentary/Permanent Outages and Duration: 38 momentary and 4 permanent • CMI (last 5 years only): 99,556 • Number of open conditions by type / defects / inspection failures: 191 open conditions on 74 unique structures • Open conditions include: Crossarms or braces with rot, woodpecker damage, and bowed conditions. • There is a three terminal line at Henry Clay substation
AEP-2020-AP002 | AEP | PJM West | 2020-01-17 | 2020-11-20 |  |  |  | Kincaid Area Project | APCO Distribution has requested a new distribution station located in Fayetteville, West Virginia. Summer projected load 11 MVA Winter projected load 13 MVA
AEP-2020-AP005 | AEP | PJM West | 2020-01-17 | 2020-04-20 | 2020-06-15 | S2250 |  | Smyth County, WV | Broadford — Wolf Hills 138 KV (~26 miles installed in the 1920’s, ~5.5 miles installed in the 1960’s) • Length: 31.54 Miles • Original Construction Type: Lattice Steel • Original Conductor Type: 82.5% 397.5 CM ACSR 30/7, 15.2% 795 CM ACSR 45/7 • Momentary/Permanent Outages: 9/1 (5 years) • Total structure count: 144 • Number of open conditions: 12 – Open conditions include: broken conductor strands, broken/burnt insulators. • Unique structure count with open conditions: 6 (7%) • Additional Info: Insulator & Hardware Corrosion: – Section Loss: The connecting elements including the tower attachment hole and the insulator hook have experienced serious section loss due to corrosion and wear. This loss of metal cross-section significantly reduces the capacity of the connection – Corrosion: The insulator caps and connecting hardware have experienced heavy to complete loss of galvanizing. When the protective galvanized coating is gone or significantly compromised the bare steel corrodes at an accelerated rate – Tower members with corrosion and damage. Lattice tower structures have little structural redundancy. A failure of one member of the structure will impact the integrity of the structure and may cause the entire tower to collapse.
AEP-2020-AP007 | AEP | PJM West | 2020-02-21 | 2020-07-17 | 2020-10-21 | s2346 |  | Baileysville Station Project | Baileysville Station • 138 kV circuit breakers G, H, I, K, L and N are SF6 filled type breakers, the only 6 of this specific type on AEP’s system • Vintage 1980s • Limited manufacturer support • Obsolete parts that are not available for replacmeent. • 46 kV CS AA is an SF6 filled 2030-69 type circuit switcher • Vintage 1990s • S&C 2030 circuit switcher has no gas monitor and sister units have a history of malfuncitons • 138 kV CS CC is an SF6 filled MARK V-138 type circuit switcher. • Vintage 1990s • This type of switcher have presented AEP with a large amount of failures and mis-operations. • Mark V family has no gas monitor • Currently 79% of the relays at Baileysville Station are in need of replacement • 28 electromechanical and 8 static type relays – These type of relays have limitations with regard to fault data collection and retention. • Capacitor Bank BB, vintage 1976, has blown fuses and defective cans. • The station has seen significant flooding; as recently as 2009 the entire station flooded. In 2001, the control house was flooded with 1.5 feet of water. • The station has insufficient room for safe ingress/egress and for accessing equipment around the station.
AEP-2020-AP016 | AEP | PJM West | 2020-02-21 | [5 empty] | Apple Grove – Point Pleasant 69 kV (17 miles) • The line consists of mainly 1960s wood pole structures. The circuit utilizes steel lattice towers with grillage foundations on the Big Sandy River Crossing. • The circuit was originally installed in 1960, primarily with 4/0 ACSR conductor and 5-bell porcelain insulators. • Structures on the line failed to meet 2017 NESC Grade B loading criteria, failed to meet current AEP structural strength requirements, and failed to meet current ASCE structural strength requirements • The insulators do not meet current AEP standards for CIFO and minimum leakage distance requirements. • There are currently 79 structures (61% of the line) with at least one open condition • A total of 171 open conditions on the line, related to damaged/worn shield wires, rotted crossarms and poles, woodpecker damage, broken or burnt insulators. • Since 2014 there have been 6 momentary and 6 permanent outages on the circuit
AEP-2020-AP017 | AEP | PJM West | 2020-02-21 | [5 empty] | Lakin – Point Pleasant 69 kV (11 miles) • The line entirely consists of 1960s wood pole structures with 4-bell porcelain insulators • Line was originally installed in 1966, with a combination of 556 ACSR and 3/0 ACSR conductor • Structures on the line failed to meet 2017 NESC Grade B loading criteria, failed to meet current AEP structural strength requirements, and failed to meet current ASCE structural strength requirements • The insulators do not meet current AEP standards for CIFO and minimum leakage distance requirements. • There are currently 95 structures (86% of the line) with at least one open condition • A total of 222 open conditions on the line, related to damaged/worn shield wires, rotted crossarms and poles, woodpecker damage, broken or missing ground wire leads, broken or loose guys. • Since 2014 there have been 17 momentary and 7 permanent outages on the circuit
AEP-2020-AP018 | AEP | PJM West | 2020-02-21 | [5 empty] | Apple Grove Station • 69 kV circuit breaker L is an FK type oil filled breaker, without oil containment. • 1960s vintage • Oil filled breakers need more maintenance due to the oil handling required and oil spills can result in significant cost associated with environmental mitigations • The manufacturer does not provide support for this type of breaker and spare parts are increasingly more difficult to obtain. • 138/69 kV transformer bank #1 was manufactured in 1965 • Elevated moisture levels • Elevated Carbon Monoxide and Carbon Dioxide levels – Indicates abnormal paper insulation deterioration • In 2004 one fan was destroyed by a failed fan blade • Oil containment inspection indicates deficiencies in the existing containment • The bank is connected directly to the 138 kV bus with a high side MOAB switch. – This can cause a fault in the station to signal the remote end breakers to open which is a known safety hazard in legacy station designs. • 54 of the 66 relays (82% of all station relays) have needs associated with them • 51 are electromechanical type and 3 are static type which have significant limitations with regards to spare part availability and fault data collection/retention • Overlapping zones of protection in existing station configuration • Apple Grove – Point Pleasant 69 kV line terminates directly into the 69 kV bus
AEP-2020-AP019 | AEP | PJM West | 2020-02-21 | [5 empty] | Point Pleasant Station • 69 kV circuit breakers G and H are an CF type oil filled breaker, without oil containment. • 1968 vintage • Oil filled breakers need more maintenance due to the oil handling required • The manufacturer does not provide support for this type of breaker and spare parts not available. • Oil spills can result in significant mitigation costs. • 69 kV circuit switcher AA is a 2030-69 type SF6 switcher. • 1991 vintage • S&C 2030 circuit switcher has no gas monitor and sister units have experienced numerous malfunctions • 39 out of the 40 relays (98% of all station relays) are in need of replacement • 34 relays are electromechanical type and 5 static type which have significant limitations with regards to fault data collection and retention.
AEP-2020-AP008 | AEP | PJM West | 2020-02-21 | 2020-04-20 | 2020-06-15 | S2251 |  | Greenup County, , KY | Kentucky Power has requested a new 69kV Transmission delivery point in Siloam area with a projected load of 9 MW.
AEP-2020-AP009 | AEP | PJM West | 2020-02-21 | 2020-12-18 |  |  |  | Pike County, KY | 46 kV Circuit Breakers A,B, and C 1960’s vintage FZO-69-1500P type oil circuit breakers. Fault Ops: CB A (33), CB B (83), and CB C (105 ). Recommended : 10 Other drivers: damage to bushings, spare part availability, historical reliability, and lack of vendor support of the breakers. There are 8 remaining FZO-69-1500P circuit breakers on the AEP system, including the 3 at this station. 86% of the relays (36/42) at the station are electromechanical, which have significant limitations with regards to fault data collection and retention and have no spare part availability due to a lack vendor support.
AEP–2020-AP011 | AEP | PJM West | 2020-02-21 | 2020-12-18 |  |  |  | Pike County, KY | Beaver Creek – Elwood 46kV: Original Install Date: 1930s vintage Length of Line: ~10.48 mi Total structure count: 60 Original Line Construction Type: Wood Conductor Type: 336 ACSR Momentary/Permanent Outages and Duration: 18 Momentary and 1 permanent Outage CMI (last 5 years only): 269,070 minutes Number of open conditions: 34 open conditions on 20 unique structures. Open conditions include crossarms and poles with rot top, woodpecker damage and leaning-in-line conditions.
AEP-2020-AP023 | AEP | PJM West | 2020-03-19 | [5 empty] | Distribution has requested a new station to be served from the Bluefield Tazewell 138 KV line. The projected peak demand is 28 MW.
AEP-2020-AP024 | AEP | PJM West | 2020-03-19 | [5 empty] | Station Meadowview Station Transformer 2 (138/69-34.5 KV): - - Transformer 2 is 39 years old with indications of brittle insulation materials - There are elevated levels of Carbon Dioxide, which is indicative of high decomposition of the paper insulating materials. - The decomposition of the paper insulation impairs the units ability to withstand short circuit or through fault events.
AEP-2020-AP025 | AEP | PJM West | 2020-03-19 | [5 empty] | Abingdon Area There is approximately 25 MVA of nontransferable load on the ~10 mile radial line between Hillman Highway Damascus stations Abingdon Hillman Highway 69 KV (installed in 1969) - Length: ~ 5 Miles - Original Construction Type: Wood - Conductor Type: 52% 4/0 ACSR 6/1 (Penguin), 20% 556,600 CM ALUM, 14% 336,400 CM ALUM 19 - Momentary/Permanent Outages: 3/8 (5 years) - Total structure count: 71 - Number of open conditions: 70 - Open conditions include: structure, broken conductor strands, broken/burnt insulators, shield wire, hardware. - Unique structure count with open conditions: 44 (62%) - Affected crossarms and poles show signs of rot, woodpecker holes, bowed, twisted conditions, broken and loose bayonets, loose, broken, and rusted guys, and loose insulators. Problem Statement (continued) Hillman Highway Saltville 69 KV (installed in 1951) - Length: ~ 23 Miles - Original Construction Type: Wood - Conductor Type: 37% 336,400 CM ACSR 30/7 (Oriole), 32% 219,900 CM ACSR 8/7 (219AC), 29% 336,400 CM ALUM 19 - Momentary/Permanent Outages: 10/5 (5 years) - Total structure count: 243 - Number of open conditions: 70 - Unique structure count with open conditions: 42 (17%) - Affected cross-arms and poles show signs of rot, woodpecker damage, leaning in-line poles, corrosion, and insect damage.
AEP-2020-AP013 | AEP | PJM West | 2020-02-21 | 2020-10-16 |  |  |  | Sullivan County, Tennessee/ Scott County, Virginia | Fort Robinson Station Circuit Breaker E (69 KV): – Circuit breaker E is 52 years old, CG/CF, oil filled type breaker without oil containment; oil filled breakers have much more maintenance required due to oil handling and spills can result in significant mitigation cost. – It has experienced 113 fault operations — exceeding manufacturer’s recommended number of 10. Circuit Breaker D (34.5 KV) Concerns: – Circuit breaker D is 36 years old, CG, oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling and spills can result in significant mitigation cost. – It has experienced 33 fault operations — exceeding manufacturer’s recommended number of 10. – CB D is 1 of only 27 remaining of the CG-48-72.5-31.5-1200 models on the AEP system. The manufacturer provides no support for the CF/CG/CGH/CH family of circuit breakers and spare parts are increasingly more difficult to obtain. This model has experienced major malfunctions associated with their OA-3 hydraulic mechanism, which includes low-pressure readings, hydraulic leaks, pump lockouts, and failure to shut off. Transformer 1 (138/69-34.5 KV) : – The current low side GOAB switch on the tertiary side of 1 Bank is incapable of load breaking. – MOAB/Ground SW configuration on the high side of the transformer. – Grounding bank is 48 years old with elevated levels of acetylene. This concentration of acetylene indicates excessive internal component decomposition due to arcing within the tank. Relay Concerns: – There are 33 electromechanical type relays (82% of all relays at the station) which have significant limitations with regards to fault data collection and retention. – There are 4 microprocessor based relays with unsupported firmware and lack of vendor support. Operations Concerns: – Fort Robinson Station is served off of the Nagel – Wolf Hills 138 kV circuit which is 39.11 miles long without CB sectionalizing
AEP-2020-AP027 | AEP | PJM West | 2020-04-20 |  |  |  |  | Roanoke & Lynchburg, VA Area | • Reusens-Roanoke 138 kV Double Circuit Line Asset (43 mi.) • Installed between 1926 and 1933 using double circuit steel lattice towers • Recent field assessments have identified severe ovalizationof holes at hanger bar connections and severe cross arm and hanger rusting as well as uniform corrosion, pitting, and deformation of steel members below grade. Evidence of steel corrosion at joints and on upper steel members was also documented. • Ferrous clamps are present on this line asset; these types of clamps can cause accelerated degradation of conductor at connection points due to excess heat generated even when operated at acceptable, rated levels. • From 2014-2018, there have been 55 momentary and 12 permanent outages on the four circuits that comprise the Reusens-Roanoke line • Cloverdale-Roanoke 138 kV Circuit* • From 2014-2018, 8 momentary and 1 permanent outage occurred resulting in 276,350 customer minutes of interruption impacting 69 MVA of peak load • Cloverdale-Reusens 138 kV Circuit* • From 2014-2018, 28 momentary and 6 permanent outages occurred resulting in 1,467,704 customer minutes of interruption impacting 39 MVA of peak load • Moseley-Roanoke 138 kV Circuit • From 2014-2018, 9 momentary and 1 permanent outage occurred • Moseley-Reusens 138 kV Circuit • From 2014-2018, 10 momentary and 4 permanent outages occurred impacting 44 MVA of load (Town of Bedford)
AEP-2020-AP028 | AEP | PJM West | 2020-04-20 |  |  |  |  | Pike County, Kentucky | Line Name: Sprigg – Stone 46kV Original Install Date (Age): 1940 Length of Line: 8.23 mi Total structure count: 55 Original Line Construction Type: Wood Majority Conductor Type: 3/0 ACSR 6/1 (Pigeon) and 2/0 COPPER Momentary/Permanent Outages and Duration: 6 Momentary and 7 permanent Outage CMI (last 5 years only): 1,119,129 minutes Line conditions: • 35 structures with at least one open condition, 64% of the structures on this circuit. • 98 structure related conditions: rotted poles, crossarms and braces, woodpecker damage, bowed braces and loose braces, affecting the crossarm, knee/ vee brace, or pole including rot, split, woodpecker, damaged, loose, and bowed conditions • 1 open conditions related to the broken strands on a jumper conductor • 9 hardware related open conditions loose or broken guy wires
AEP-2020-AP029 | AEP | PJM West | 2020-04-20 |  |  |  |  | Johnson County, Kentucky | Line Name: Kenwood – Van Lear 46kV Original Install Date (Age): 1969 Length of Line: 1.77 mi Total structure count: 11 Original Line Construction Type: Wood Conductor Type: 336,400 ACSR 26/7 Line conditions: • 3 of the 11 structures have conditions that comprise 27% of the line section. • Open conditions include: rot and woodpecker damage. • Kenwood Station is currently radially fed with a peak load near 22 MVA. Van Lear Switch: • The switches at Van Lear have been tagged as inoperable and unsafe to operate. The old hydraulic type mechanism on these switches does not operate properly, arcing horns are burnt off, and operating rod supports are damaged.
AEP-2020-AP030 | AEP | PJM West | 2020-04-20 |  |  |  |  | Kingsport, TN | Appalachian Power Co. (Distribution) has requested adding a new 25 MVA 138/12KV transformer at Eden’s Ridge Station to serve growing load in the Kingsport area.
AEP-2020-AP031 | AEP | PJM West | 2020-05-22 | [5 empty] | Clifford Station: 138/69/46 kV Transformer #1 1963 Vintage Transformer Elevated levels of Acetylene have been documented indicating increased decomposition of the paper insulating materials. The presence of acetylene indicates electrical discharge faults of high energy have occurred within the main tank causing electrical breakdown of the unit. Due to deteriorated gaskets at the radiator headers, this unit is leaking oil. 138/46 kV Transformer #3 1950 Vintage Transformer An upward trend in insulation power factor indicates an increase in particles within the oil and the dielectric strength of the insulation system (oil and paper) are in poor condition, impairing the unit’s ability to withstand electrical faults.
AEP-2020-AP032 | AEP | PJM West | 2020-06-19 |  |  |  |  | Scottsville, VA Area | Scottsville Station: 138/46 kV Transformer #1 (connected in parallel with T2) 1950 Vintage Transformer Unit has low levels of dielectric strength, indicating an increase in particles within the oil which decreases the ability to withstand fault events, leading to damage to the paper insulation. Observed high oil power factor and low oil dielectric strength are strong indications of elevated moisture in the oil. 138/46 kV Transformer #2 (connected in parallel with T1) 1954 Vintage Transformer Elevated levels of carbon dioxide and ethane indicate excessive decomposition of the paper insulating materials. An upward trend in insulation power factor indicates an increase in particles within the oil and the dielectric strength of the insulation system (oil and paper) are in poor condition, impairing the unit’s ability to withstand electrical faults. 138/46 kV Transformer #5 1950 Vintage Transformer The paper insulating material is deteriorating, reducing the ability of the transformer to withstand through fault events, which could potentially lead to catastrophic failure.
AEP-2020-AP033 | AEP | PJM West | 2020-05-22 | [5 empty] | Roanoke Station: 138/69/12 kV Transformer #5 1981 Vintage Transformer Elevated levels of carbon monoxide, carbon dioxide and hydrogen indicate excessive levels of decomposition of the paper insulating materials. 138 kV Circuit Switchers BB and CC Both are 1990’s vintage The Mark V family of circuit switchers have no gas monitor and currently in-service units on the AEP system have experienced 110 malfunctions from May 2000 to August 2019. Failed operational components including high contact resistance, gas loss, and interrupter failure represent half of these malfunctions. Two malfunctions of note were catastrophic equipment failures involving failures to trip. 138 kV Capacitor Bank CC and 34.5 kV Capacitor Bank AA Leaking around bushings on both banks 6 cans are failed on bank CC 69 kV Circuit Breakers U and V 1970’s Vintage Circuit Breakers These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require Circuit breaker U has each exceeded the manufacturer’s designed number of full fault operations (12) Roanoke Station: Relaying Roanoke Substation currently deploys 103 relays, implemented to ensure the adequate protection and operation of the substation. Currently, 79 of the 103 relays (77% of all station relays) are in need of replacement. There are 50 electromechanical and 8 static which have significant limitations with regards to fault data collection and retention. These relays lack vendor support and have little to no access to spare parts. There are 3 DPU microprocessor type relays on the three distribution breakers. The DPU relays pose a potential safety risk to persons performing breaker operation because the DPUs are mounted directly on the circuit breaker without a delay for opening and closing the breaker. There are 18 microprocessor relays that utilize legacy firmware. Pilot Wire Pilot wire relaying exists on the Campbell Ave. 69 kV, Roanoke 69 kV and Campbell Ave 34.5 kV circuits TFS lacks adequate crew training and experience on handling pilot wire; only a small number of crews are available with necessary experience to perform corrective maintenance High corrective maintenance costs are incurred (P&C, line, forestry, build roads, etc.) High-Side Transformer Protection No automatic high-side protection exists on transformer #5 or #2 Both are directly connected to 138 kV bus #2, which would operate five 138 kV circuit breakers for a transformer fault
AEP-2020-AP034 | AEP | PJM West | 2020-05-22 | [5 empty] | Centerville Station: 69 kV Circuit Breaker B 1970’s Vintage Circuit Breaker Oil filled breaker without oil containment. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. This circuit breaker, has exceeded the manufacturer’s designed number of full fault operations (108) High-side Transformer MOAB Ground Switch (138/69/12 kV T1) is used for high-side transformer protection There is a three terminal line configuration through the Town of Bedford 69 kV loop. The flip-flop configuration connection to the double circuit 138 kV line that runs adjacent to the station is a source of operational and protection challenges when faults occur. Relaying Centerville Substation currently deploys 26 relays, implemented to ensure the adequate protection and operation of the substation. Currently, all 26 of the relays (100% of all station relays) are in need of replacement. There are 21 of the electromechanical which have significant limitations with regards to fault data collection and retention. These relays lack vendor support and have little to no access to spare parts. Also, the remaining 5 relays that are microprocessor based from utilize legacy firmware.
AEP-2020-AP035 | AEP | PJM West | 2020-06-19 |  |  |  |  | Washington, Virginia | Meadowview Station Circuit Breakers F&G (69 KV) Concerns: Circuit Breakers F and G are 23 years old, 72PM31-20 type, SF6 filled breakers. Circuit Breakers F and G have experienced 88 and 72 total fault operations, respectively, exceeding manufacturer’s recommended number full fault operations of 6. Circuit breakers of this type across the AEP system have had reports of moisture ingress into the breaker tank, which leads to increased maintenance and a higher risk of failure. This model type of breakers have experienced five catastrophic failures. There are documented issues with failures to close due to burned up coils, and 98 malfunction records related to SF6 gas leaks.
AEP-2020-AP036 | AEP | PJM West | 2020-07-17 |  |  |  |  | Roanoke, VA Area | • Distribution requested a new station (Winston Avenue) located just south of the Hancock-Walnut Avenue 69 kV circuit to serve load currently fed from Walnut Avenue Station, which is located in the flood way of the Roanoke River as determined by FEMA and the Army Corps of Engineers. There have been several instances in the last three years where prolonged periods of rain have resulted in water levels that reached the bottom of the breaker control cabinets in the station. • Medical and Health Facilities load continues to grow in the area served by Walnut Avenue Station. The main feed for Roanoke Memorial Hospital (RMH) is the Walnut Avenue/South Roanoke 12 kV feeder. RMH has plans to construct a new 15 story (2 MVA) expansion at nearby Crystal Springs along with a renovation/relocation of their existing Cancer Center by April 2024. The load on the South Roanoke 12 kV feeder is projected to reach 8.9 MVA, or 69% of its 12.9 MVA capability by summer 2024. This load is primarily RMH and while the concern is not necessarily related to a projected overload, it is about having Roanoke’s largest hospital served by a main feed in the Roanoke River Floodway and its alternate feed (Wasena/Wiley 12kV) in the Roanoke River Floodplain. • The Walnut Avenue/Maher Ave 12 kV feeder has seen and will continue to see Medical and Health Facilities growth. Recent additions have been the Virginia Tech School of Medicine, Carilion Biomedical center for which the first of three planned expansions was announced for 6/2020. The load on the Maher Avenue 12 kV feeder is projected to reach 9.1 MVA, or 80% of its 11.4 MVA capability by summer 2024. While the concern is not necessarily related to a projected overload, cold load pickup is a concern following an outage when trying to restore power on a 12 kV feeder when its load exceeds 9.0 MVA.
AEP-2020-AP037 | AEP | PJM West | 2020-07-17 |  |  |  |  | Smyth County, VA | Station Name: Saltville Circuit Breakers A, B, C, L & V (138 KV) Concerns: • All of these breakers are HVB145-40000. These breakers are of either 1996 (A & B) or 2001 (C, L, & V) vintage. • These CBs require maintenance beyond the typical SF6 model type because of air trip mechanisms. The entire air system must be rebuilt whenever maintenance is performed resulting in significant costs. • All of these breakers have exceeded the manufacturer’s designed number of full fault operations –Breakers A, B, C, L, V have experienced 51, 75, 12, 22, 70 fault operations, respectively —exceeding manufacturer’s recommended number of 10. Circuit Breakers J (69 KV) Concerns: • Circuit breaker J is 53 years old, CF-48-69-2500 type, oil filled breaker – which requires frequent maintenance. Oil spills are common and can result in significant environmental mitigation costs. • This breaker has experienced 34 fault operations — exceeding manufacturer’s recommended number of 10. • There is no support for the CF family of circuit breakers and spare parts are obsolete, impossible to obtain. Transformer Bank 1 (138/ 69-34.5 KV) Concerns: • The 138/ 69-34.5 KV Transformer Bank is 53 yeas old with no oil containment • This unit shows elevated levels of Carbon Dioxide and Ethane, which are currently at IEEE Level 3 and 4, respectively. These levels indicate excessive decomposition of the paper insulating materials. • The presence of Carbon Dioxide and Ethane indicates decomposition of the paper insulation that impairs the unit to withstand future short circuit or through fault events due to the state of the paper insulation. • The low side surge arresters (on 69KV) are obsolete and in need of replacement. Other station concerns: • The station yard is tiered with stairs to access the different levels which creates a washout risk. • Power transformers XF#1, XF#2, and XF#5 are connected directly to 138kV bus through MOABs — which renders Saltville bus#1 and bus#2 to a transformer fault. Moreover, malfunction record indicated that the MOAB X1 would not open during trip testing due to the plunger sticking on the contactor. Also, MOAB X2 is on cap and pin insulators. • Perimeter fence is not standard height and damaged. • Concrete cable trench along retaining wall is damaged. • Several foundations throughout station are degraded. • Lower elevation levels in the station yard are in the 100-year flood plain of the nearby New River. • Asbestos and lead paint in both of the control buildings. Relay concerns: • Currently, 79 of the 95 relays are in need of replacement. • There are 68 of the electromechanical, 6 static type and 5 legacy microprocessor relays — which have significant limitations with regards to fault data collection and retention.
AEP-2020-AP014 | AEP | PJM West | 2020-02-21 | 2020-10-16 |  |  |  | Sullivan County, Tennessee/ Scott County, Virginia | Hill Station Circuit Breaker H (69 KV): – Circuit breaker H is 52 years old, CF model type, oil filled type breaker filled without oil containment; oil filled breakers have much more maintenance required due to oil handling and oil spills can result in significant mitigation cost. Spare parts for these units are difficult to impossible to procure. – 91 fault operations — exceeding manufacturer’s recommended number of 10. Circuit Switcher AA (69 KV): – Circuit switcher AA is 25 years old, 2030-69, SF6 type breaker. This type of circuit switcher has no gas monitor and sister units have a history of malfunctions, including gas loss, interrupter failures, and operating mechanism failures. Transformer 1 (138/69-34.5 KV) Concerns: – Transformer bank 1 is 63 years old with elevated levels of carbon dioxide and moisture and a decrease in dielectric strength. – The current MOAB/Ground SW configuration on the high side of the transformer Relays – 20 relays (53%) are of the electromechanical type which have limitations with regards to fault data collection and retention. – These relays lack vendor support and have no access to spare parts. Operations Concerns: – Hill Station is served off of the Clinch River – Nagle 138 kV circuit which is 41.61 miles long without CB sectionalizing.
AEP-2020-AP015 | AEP | PJM West | 2020-02-21 | 2020-10-16 |  |  |  | Sullivan County, Tennessee/ Scott County, Virginia | Fort Robinson —Hill 69 KV (installed in 1970) Length: 12.7 ~14.2 Miles Original Construction Type: Wood (86% original) Original Conductor Type (91% original): 219.9 ACSR, 1/0 CU, 336 ACSR, 4/0 ACSR, and 556 ACSR Momentary/Permanent Outages: 7 momentary, 8 permanent (5 years) CMI: 5,721,762 Total structure count: 127 213 Number of open conditions: 120 Open conditions include: broken conductor strands, broken/burnt insulators, split Bayonet, cracked X-Brace. Unique structure count with open conditions: 95 (44%) Additional Info: There have been 5 weather related momentary outages, with 4 of those being attributed to lightning as well as 1 permanent outage. These lightning caused outages are indicative of insufficient shielding and/or insufficient grounding Note: ~1.5 mile 1/0 Cu conductor section of the ~ 5 miles Fort Robinson – Moccasin Gap 69 KV line section will be addressed as part of b3101
AEP-2020-AP020 | AEP | PJM West | 2020-03-19 | 2020-04-20 | 2020-06-15 | S2252 |  | Salem, VA | AEP Distribution is requesting redundant service for a new critical and sensitive load in the Roanoke region, approximately 0.6 MW total.
AEP-2020-AP041 | AEP | PJM West | 2020-10-16 |  |  |  |  | Lynchburg, VA Area | AEP Distribution is requesting a new 138/12 kV transformer at Reusens station to transfer load from Peakland and Boonsboro stations due to the following concerns: Peakland station site inadequate for significant expansion (size & terrain) and is currently served by a radial tap from Reusens – Dearington 69 kV line. Both Peakland 12 kV circuits are loaded over 90% summer capacity Boonsboro 138/12 kV, 20 MVA transformer loaded over 90% in winter Boonesboro 12 kV circuit projected to overload by summer 2025
AEP-2020-AP042 | AEP | PJM West | 2020-11-20 |  |  |  |  | Fayette/Raleigh County, WV | Bradley – Layland 69 kV (14.25 miles) • Circuit is comprised mostly of wood pole structures • 1930s vintage structures (81%) • Circuit fails to meet 2017 NESC Grade B loading criteria, AEP structural strength requirements, and fails to meet current ASCE structural strength requirements • 4-bell porcelain insulators do not meet current AEP Standards • 39 structures with at least one open condition (38% of the structures) • Structure conditions include rot top, insect damage, woodpecker holes • Since 2014, there have been 30 momentary and 23 permanent outages on the Bradley - Layland 69 kV circuit • Majority of the momentary outages were due to weather including lightning/wind • Outages resulted in approximately 984k customer minutes of interruption
AEP-2020-AP043 | AEP | PJM West | 2020-11-20 |  |  |  |  | Kanawha County, WV | Cabin Creek –London 46 kV (8.35 miles) • Circuit is comprised primarily of 1913 vintage lattice steel (38%), 1999 vintage wood (27%) and 2011 vintage steel (29%) • Line was originally constructed in 1913 • Circuit fails to meet 2017 NESC Grade B loading criteria, AEP structural strength requirements, and fails to meet current ASCE structural strength requirements • 4-bell porcelain insulators do not meet current AEP Standards • Conductor on the line is primarily 3/0 and 4/0 Copper • The circuit is located along the Kanawha River and has a history of landslides • 9 Structures with at least one open condition (7% of the line) • 13 structural conditions include rot top, insect damage, woodpecker holes, bent/damaged steel lacing • 58 hardware conditions related to rusted/corroded shielding and conductor hardware, broken insulators and guys, worn/cracked conductor hardware • Since 2014, there have been 9 momentary and 1 permanent outages on the Cabin Creek –London 46 kV circuit • Majority of the momentary outages were due to weather including lightning/wind • Permanent outages were caused by vegetation fall-in from outside the ROW, flood/slides, lightning/ice/snow • Outages resulted in approximately 10k customer minutes of interruption • There are a significant number of landslides along the length of this line. Known slides have occurred in the last 10 years. The terrain along the line is very rough and mountainous.
AEP-2020-AP044 | AEP | PJM West | 2020-11-20 |  |  |  |  | Logan County, West Virginia | Line Name: Becco – Pine Gap 46kV Original Install Date (Age): 1930 Length of Line: ~20.79 mi Total structure count: 160 Original Line Construction Type: Wood Conductor Type: 3/0 ACSR, 176,900 ACSR, 1/0 COPPER, 336,400 ACSR Momentary/Permanent Outages and Duration: 19 Momentary and 8 permanent Outage CMI (last 5 years only): 1,790,749 minutes Line conditions: Becco – Pine Gap 46kV: • 35 structures with at least one open condition, 21% of the structures on this circuit. • 32 structure related open conditions : affecting the crossarm, knee/ vee brace, or pole including rot, damaged, and insect damage conditions. • 3 guy wire related open conditions including: Loose, Broken, damaged. • 117 of 160 structures are 1930s wood vintage • 148 of 160 structures are wood construction
AEP-2020-AP045 | AEP | PJM West | 2020-11-20 |  |  |  |  | Kanawha County, WV | London Station • 46 kV CB-B • 1988 vintage • The breaker is oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling. Oil spills are common and can result in significant environmental mitigation costs. • 53 total fault operations • 46 kV CB-F • 1968 vintage • The breaker is oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling. Oil spills are common and can result in significant environmental mitigation costs. • 15 total fault operations • London station currently deploys 35 relays • 33 out of 35 relays are in need of replacement (94%) • 28 are electromechanical relays which have significant limitations with regards to fault data collection • 5 of the microprocessor relays utilize legacy firmware • Control House • Asbestos/lead paint is present in the control house • Access road to the station severely limits the ability to deliver large equipment to the station • 46 kV bus shows significant signs of rust on lattice members and on bolts
AEP-2020-AP046 | AEP | PJM West | 2020-11-20 |  |  |  |  | Scottsville, VA Area | – AEP APCo Distribution is requesting additional load serving capability at Scottsville Station, including a new feeder exit and larger transformer, to serve as a backup source for the load served out of Esmont station. – Esmont station will be radially fed after the completion of b3208 due to the retirement of the 46 kV line towards Clifford. This request is to provide additional flexibility for the customers served from Esmont. – 46 kV Circuit Breaker E: • 72EPB-31.5-20 Type, SF-6 filled breaker manufactured in 1992 • This circuit breaker has experienced 116 fault operations, exceeding the manufacturer’s designed number of 15 full fault operations. Each of these fault operations is likely not at the full fault current rating of the circuit breaker, but with each fault operation of any magnitude comes accelerated aging. • Since 2003, there have been 24 gas leak malfunction records associated with CB E at Scottsville • These model types have historically exhibited bad gas leaks, bushing failures, and CT cores getting wet
AEP-2020-AP047 | AEP | PJM West | 2020-12-18 |  |  |  |  | Perry County, KY | Hazard – Bonnyman 69kV #1. Original Install Date (Age): 1940. Length of Line: 9.5 mi. Total structure count: 49. Original Line Construction Type: Wood. Conductor Type: 336,400 ACSR. Momentary/Permanent Outages and Duration: 10 Momentary and 3 permanent Outage. CMI (last 5 years only): 185,875 minutes. Line Conditions: 22 structures with at least one open condition, 45% of the structures on this circuit. 45 structure related open conditions: crossarms and poles including rot, damaged, insect damaged, woodpecker hole, burnt, and bowed conditions. 3 shield wire conditions with damaged and broken strands.1 broken ground wire lead. 2 broken insulators.
AEP-2020-IM001 | AEP | PJM West | 2020-02-21 | [5 empty] | Berrien Springs-Colby 69kV line • 15.72 miles of wood pole structures with horizontal insulators rebuilt in 1995 • 148 structures with at least one open condition, 31% of the structures on the line • Open conditions include insect or woodpecker damage, broken or stolen ground wire conditions, and broken or burnt insulators • Outages: 2 permanent since 2015
AEP-2020-AP021 | AEP | PJM West | 2020-04-20 | 2020-09-11 | 2021-01-13 | s2397.1-.5 |  | South Point – West Huntington | South Point – West Huntington 34.5 kV Line (~11 miles) • The line consists of mainly wood pole (79%) structures in addition to steel (12%) and lattice steel (9%) structures. • The line was originally built in 1926 (69%) and 1930 (10%) primarily with 4/0 copper conductor. • Structures on the line failed to meet 2017 NESC Grade B loading criteria, failed to meet current AEP structural strength requirements, and failed to meet current ASCE structural strength requirements • Current shielding on the majority of the line does not meet current standards. • There are currently 93 structures (62% of the line) with at least one open condition • A total of 159 structural open conditions on the line primarily related to pole and crossarm rot. Other structure conditions include woodpecker damage, split crossarms/poles and bowed crossarms/poles. • There are 54 shielding and grounding related open conditions including missing ground wire leads, damaged shield wire and broken ground wire leads. • There are an additional 15 open conditions related to burnt/broken insulators and guy wire. • Since 2014 there have been 4 permanent outages on the circuit due to arrestor failure, wind, switch failure and vegetation contact from outside the ROW. The outages resulted in a total of 198k customer minutes interrupted.
AEP-2020-IM003 | AEP | PJM West | 2020-02-21 | [5 empty] | Buchanan Hydro Station: • Buchanan Hydro station has flooded twice in the last 5 years causing the 12kV load to be dropped from the station. • (2) FK-type Oil filled breakers, AEP has common failure modes for these types of breakers with compressor failures, valve defects, reclose failures and charging motor failures. • Both breakers installed in 2003 • Breaker A has exceeded the designed number of fault operations • (2) CF-Type oil filled breakers. This model family has experienced major malfunctions associated with their hydraulic mechanisms which have led to several failures to close and other types of mis-operations. • Both breakers have exceed the designed number of fault operations • Transformer #1 was installed in 1964. The transformer has elevated levels of carbon dioxide and ethylene, there is indication of overheating faults occurring in the main tank which have further degraded the insulating paper materials. There is also indication of capacitive layer deterioration. • Transformer #2 was installed in 1965. The age of the unit’s insulation materials can lead to susceptibility of short circuit faults which may cause failure in the main tank. The transformer has elevated levels of carbon dioxide and ethylene, there is indication of overheating faults occurring in the main tank which have further degraded the insulating paper materials Buchanan Hydro –Clark Equipment Tap 34.5kV: • 1.36 miles of 1954 and 1984 wood pole cross arm line • 10 unique structures (26%) with at least one open condition • Open conditions include pole or cross arm with rot conditions
AEP-2020-AP022 | AEP | PJM West | 2020-03-19 | 2020-04-20 | 2020-06-15 | S2253 |  | Pike County, Kentucky | AEP Kentucky Power Distribution has requested a new distribution service out of the Cedar Creek John Creek 138kV circuit near Pikeville, Kentucky. The projected Winter peak projected load is 13 MVA.
AEP-2020-AP023 | AEP | PJM West | 2020-03-19 | 2021-01-15 |  |  |  | Bluefield, VA | Distribution has requested a new station to be served from the Bluefield — Tazewell 138 KV line. The projected peak demand is 35 28MW.
AEP-2020-IM006 | AEP | PJM West | 2020-02-21 | [5 empty] | McKinley 138/69/34.5kV • Breakers G 34kV • 1956 vintage Oil breakers • Fault Operations: G(10) – Recommended(10) • Oil filled breakers have much more maintenance required due to oil handling that modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported. Oil spills can result in significant costs associated with mitigation. McKinley – Spy Run 34.5kV line asset (~5 miles) • 1960 vintage wood crossarm construction • There are currently 42 open conditions on this line across 37 unique structures (27% of the line) including, but not limited to, split crossarms, rot top, rot heart and broken grounds. • Structures are in the river flood plains and in the flood control berm
AEP-2020-IM007 | AEP | PJM West | 2020-02-21 | [5 empty] | Moorepark 69kV Tap line: • 9.02 miles of 1967 wood pole structure with horizontal insulators • 94 structures with at least one open condition (52% of the line) • Open conditions include pole damage such as cracked, insect damage, rot heart and woodpecker holes, shielding/grounding conditions related to broken, missing or stolen ground wires, and broken or burnt insulators • Since 2014 8 momentary and 1 permanent outages • 7 due to weather (lightning/thunderstorm) demonstrating poor shielding • This line is a three terminal line which is hard to coordinate from a relaying perspective and is prone to misoperations Moorepark (138/69kV) Station: • 69kV circuit breaker (1) installed in 2006 with 41 documented malfunction records due to low SF6. This breaker has exceeded the designed number of fault operations. • (1) 2030-69 Cap Switcher with no gas monitor. The AEP system has experienced numerous malfunctions of this type of cap switcher due to gas loss, interrupter failures, operating mechanism failures and trip or reclose failures.
AEP-2020-AP024 | AEP | PJM West | 2020-03-19 | 2020-12-18 |  |  |  | Washington, Virginia | Station Meadowview Station Transformer 2 (138/69-34.5 KV): Transformer 2 is 39 years old with indications of brittle insulation materials There are elevated levels of Carbon Dioxide, which is indicative of high decomposition of the paper insulating materials. The decomposition of the paper insulation impairs the unit’s ability to withstand short circuit or through fault events.
AEP-2020-IM009 | AEP | PJM West | 2020-02-21 | [5 empty] | Bridgman-Pletcher 69kV line: • 7.7 miles of 1964 wood pole line • 57 unique structures (46%) with at least one open conditions relating to structure and conductor issues • Open conditions include rotted poles, burnt or broken insulators, split or damaged poles or broken conductor strands, woodpecker damage and guy/ground wire damage
AEP-2020-AP025 | AEP | PJM West | 2020-03-19 | 2020-12-18 |  |  |  | Washington, Virginia | Abingdon Area There is approximately 25 MVA of nontransferable load on the ~10 mile radial line between Hillman Highway – Damascus stations Abingdon — Hillman Highway 69 KV (installed in 1969) Length: ~ 5 Miles Original Construction Type: Wood Conductor Type: 52% 4/0 ACSR 6/1 (Penguin), 20% 556,600 CM ALUM, 14% 336,400 CM ALUM 19 Momentary/Permanent Outages: 3/8 (5 years) Total structure count: 71 Number of open conditions: 70 Open conditions include: structure, broken conductor strands, broken/burnt insulators, shield wire, hardware. Unique structure count with open conditions: 44 (62%) Affected crossarms and poles show signs of rot, woodpecker holes, bowed, twisted conditions, broken and loose bayonets, loose, broken, and rusted guys, and loose insulators.Hillman Highway — Saltville 69 KV (installed in 1951) Length: ~ 23 Miles Original Construction Type: Wood Conductor Type: 37% 336,400 CM ACSR 30/7 (Oriole), 32% 219,900 CM ACSR 8/7 (219AC), 29% 336,400 CM ALUM 19 Momentary/Permanent Outages: 10/5 (5 years) Total structure count: 243 Number of open conditions: 70 Unique structure count with open conditions: 42 (17%) Affected cross-arms and poles show signs of rot, woodpecker damage, leaning in-line poles, corrosion, and insect damage.
AEP-2020-AP026 | AEP | PJM West | 2020-03-19 | 2020-11-20 |  |  |  | Leslie, Clay, Bell and Knox Counties, Kentucky | Line Name: Wooton – Pineville 161kV Line Section: Leslie – Pineville 161kV Original Install Date (Age): 1942 Length of Line: ~34.24 mi Total structure count: 189 Original Line Construction Type: Wood Conductor Type: 500 KCM COPPER Momentary/Permanent Outages and Duration: 12 Momentary and 5 permanent Outage CMI (last 5 years only): 26,096 minutes Line conditions: Leslie – Pineville line section: • 130 structures with at least one open condition, 69% of the structures on this circuit. • 221 structure related open conditions : affecting the crossarm, knee/ vee brace, or pole including rot, split, woodpecker, damaged, loose, and bowed conditions • 2 open conditions related to the shielding wire, including broken strands • 3 hardware related open conditions related to insulator, conductor hardware, or shield wire hardware, including broken, missing bolt, and worn Line Section: Wooton – Leslie 161kV Original Install Date (Age): 1942 Length of Line: ~4.68 mi Total structure count: 23 Original Line Construction Type: Wood Conductor Type: 500 KCM COPPER Momentary/Permanent Outages and Duration: none in last five years CMI (last 5 years only): none in last five years Line conditions: Leslie – Wooton line section: • 17 structures with at least one open condition, 74% of the structures on this section. • 32 structure related open conditions including: crossarm or pole including rot, insect damage and woodpecker damage
AEP-2020-AP028 | AEP | PJM West | 2020-04-20 | 2021-01-15 |  |  |  | Pike County, Kentucky | Line Name: Sprigg – Stone 46kV Original Install Date (Age): 1940 Length of Line: 8.23 mi Total structure count: 55 Original Line Construction Type: Wood Majority Conductor Type: 3/0 ACSR 6/1 (Pigeon) and 2/0 COPPER Momentary/Permanent Outages and Duration: 6 Momentary and 7 permanent Outage CMI (last 5 years only): 1,119,129 minutes Line conditions: 35 structures with at least one open condition, 64% of the structures on this circuit. 98 structure related conditions: rotted poles, crossarms and braces, woodpecker damage, bowed braces and loose braces, affecting the crossarm, knee/ vee brace, or pole including rot, split, woodpecker, damaged, loose, and bowed conditions 1 open conditions related to the broken strands on a jumper conductor 9 hardware related open conditions loose or broken guy wires
AEP-2020-AP030 | AEP | PJM West | 2020-04-20 | 2020-12-18 |  |  |  | Kingsport, TN | Appalachian Power Co. (Distribution) has requested adding a new 25 MVA 138/12KV transformer at Eden’s Ridge Station to serve growing load in the Kingsport area.
AEP-2020-AP031 | AEP | PJM West | 2020-05-22 | 2020-12-18 |  |  |  | Clifford, VA Area | Clifford Station: 138/69/46 kV Transformer #1 1963 Vintage Transformer Elevated levels of Acetylene have been documented indicating increased decomposition of the paper insulating materials. The presence of acetylene indicates electrical discharge faults of high energy have occurred within the main tank causing electrical breakdown of the unit. Due to deteriorated gaskets at the radiator headers, this unit is leaking oil. 138/46 kV Transformer #3 1950 Vintage Transformer An upward trend in insulation power factor indicates an increase in particles within the oil and the dielectric strength of the insulation system (oil and paper) are in poor condition, impairing the unit’s ability to withstand electrical faults.
AEP-2020-IM018 | AEP | PJM West | 2020-05-22 | [5 empty] | Van Buren 138/69/12kv station 138/69/12 kV Transformer #1 1967 vintage Elevated moisture levels Increased cost of maintenance due to leaking Increased levels of decomposition of the paper insulating materials, leading to increased risk of failure Breaker B 69kV 1964 vintage oil filled, CF-type breaker. This type is oil filled without oil containment. Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is not possible due to these models no longer being vendor supported Van Buren is part of a three-terminal line configuration with the Delaware – Sorenson 138kV circuit.
AEP-2020-AP032 | AEP | PJM West | 2020-05-22 | 2020-12-18 |  |  |  | Scottsville, VA Area | Scottsville Station: 138/46 kV Transformer #1 (connected in parallel with T2) 1950 Vintage Transformer Unit has low levels of dielectric strength, indicating an increase in particles within the oil which decreases the ability to withstand fault events, leading to damage to the paper insulation. Observed high oil power factor and low oil dielectric strength are strong indications of elevated moisture in the oil. 138/46 kV Transformer #2 (connected in parallel with T1) 1954 Vintage Transformer Elevated levels of carbon dioxide and ethane indicate excessive decomposition of the paper insulating materials. An upward trend in insulation power factor indicates an increase in particles within the oil and the dielectric strength of the insulation system (oil and paper) are in poor condition, impairing the unit’s ability to withstand electrical faults. 138/46 kV Transformer #5 1950 Vintage Transformer This transformer is the source for documented excessive sound and complaints from nearby home owners, which required a sound abatement wall.
AEP-2020-IM020 | AEP | PJM West | 2020-08-14 |  |  |  |  | AM General-Twin Branch-Kline 34.5kV | AM General-Twin Branch-Kline 34.5kV 1 mile of 1950’s wood pole cross arm construction 7 structures, 28% of the line, with open conditions Open conditions include: pole rot, broken or missing ground lead wires The grounding method utilizes butt wraps which is not current AEP standards During field assessment structures were found with vertical pole splitting, decay to cross arms, rot top, and upper pole decay
AEP-2020-IM021 | AEP | PJM West | 2020-09-11 |  |  |  |  | East Elkhart- Mottville Hydro- Corey 138kV | East Elkhart- Mottville Hydro- Corey 138kV 16.3 miles consisting of 1960’s wood pole H frame structures with vertical insulators 88% of structures are original 100% of conductor is original Since 2014 there have been 3 momentary outages on Corey-Mottville Hydro 138kV 2 momentary outages on East Elkhart-Mottville Hydro 138kV The line contains 36 open conditions including burnt or broken insulators and broken or missing ground lead wire Leads to poor lightning performance (3 outages caused by lightening) Shielding angle does not meet current AEP shielding requirements The grounding utilizes butt wraps which are not current AEP standards Field assessment found 45% of the structures assessed with at least one condition. Conditions included cracked and split cross arms, upper pole and knee brace decay, woodpecker damage and flashed insulators Insulators don’t meet CIFO and minimum leakage requirements
AEP-2020-IM022 | AEP | PJM West | 9/11/2020, 10/6/2020 |  |  |  |  | South Butler Load Increase | At South Butler 345kV station, the customer has requested delivery for a 10 MW load increase served by a new transformer at the station.
AEP-2020-IM023 | AEP | PJM West | 2020-11-20 |  |  |  |  | Pettit Ave – Melita 69kV | • Pettit Ave – Melita 69kV ~1.84 Miles • Originally constructed in 1967 • Wood pole construction with 61/62 structures original from 1967. • Recent field inspection identified 48 of the 62 structures on the line have moderate to advanced decay or shell damage. • Additional conditions include insect damage and stolen/missing ground leads along with the rot top and/or shell decay on the structures. • Structures do not meet 2017 NESC Grade B loading criteria, do not meet current AEP structural strength requirements, and do not meet the current ASCE structural strength requirements.
AEP-2020-IM024 | AEP | PJM West | 2020-11-20 |  |  |  |  | Illinois Road Transformer | Illinois Road 138/69kV Station: 138/69/12kV Transformer 1 • Manufactured in 1980 • Transformer is showing elevated moisture levels, low levels of Interfacial Tension and an increasing trend in Power Factor. • This level of moisture is an indication of gasket leaks and breakdown in oil or paper insulation. • The low level of Interfacial Tension is an indication acid has coated the insulation and sludge is ready to deposit within the main tank. • The upward trend in PF indicates that there is an increase in particles in the oil.
AEP-2020-IM025 | AEP | PJM West | 2020-11-20 |  |  |  |  | Industrial Park Transformer | Industrial Park 138/69/34.5kV Station: 138/69/34.5kV Transformer 1 • Manufactured in 1967 • Transformer has increased levels of CO2 indicated in the dissolved gas analysis. • Level of CO2 indicates decomposition of the paper insulating materials which impairs units ability to withstand faults. • The downward Interfacial Tension trend paired with upward power factor trend indicate that there are increased particles within the oil, which decreases the dielectric strength of the transformer. • Doble tests on the bushings indicate changes in the bushing power factor and capacitance. This change indicates these bushings are at a greater risk of failure.
AEP-2020-IM026 | AEP | PJM West | 2020-11-20 |  |  |  |  | Kendallville Transformer | Kendallville 138/69kV Station: 138/69kV Transformer 1 • Manufactured in 1971 • Transformer has increased levels of Ethane and CO2 indicated in the dissolved gas analysis • Increased levels of CO2 and Ethane indicates decomposition of the paper insulating materials, which impairs the units ability to withstand faults. • The downward Interfacial Tension trend paired with upward power factor trend and increased moisture content indicate that there are increased particles within the oil, decreasing the dielectric strength of the transformer
AEP-2020-AP035 | AEP | PJM West | 2020-03-19 | 2020-12-18 |  |  |  | Washington, Virginia | Meadowview Station Circuit Breakers F&G (69 KV) Concerns: Circuit Breakers F and G are 23 years old, 72PM31-20 type, SF6 filled breakers. Circuit Breakers F and G have experienced 88 and 72 total fault operations, respectively, exceeding manufacturer’s recommended number full fault operations of 6. Circuit breakers of this type across the AEP system have had reports of moisture ingress into the breaker tank, which leads to increased maintenance and a higher risk of failure. This model type of breakers have experienced five catastrophic failures. There are documented issues with failures to close due to burned up coils, and 98 malfunction records related to SF6 gas leaks.
AEP-2020-AP038 | AEP | PJM West | 2020-07-17 | 2020-11-20 |  |  |  | Rocky Mount, VA Area | • Grassy Hill Loop and Tank Hill Tap 138 kV Line Asset (1.3 mi.) • The single circuit wood pole structures that make up 0.95 miles of the 1.3 mile long Grassy Hill Loop and Tank Hill Tap 138 kV Line Asset are the focus of the concern. • Recent field assessments have identified severe Woodpecker holes and cracking damage, accounting for 67% of the 12 single pole structures on the radial line. • Weather cracks range in size from 2 to 7 feet in length, with many poles having multiple. • Woodpecker holes range in size from 1 to 5 inches in diameter and the poles have 10 to 30 of them. • A pole appears to be hollow on the inside. • A pole has mold on the upper portion, that is 10 feet in length. • The radial line feeds sensitive industrial customers in the Rocky Mount, VA area. These customers operate 24 hours a day and do not take outages. The Tank Hill station that is fed from the Fieldale – Roanoke line is the only station that can handle the industrial load. • From 2015, there have been 6 momentary and 2 permanent outages on the associated Fieldale - Roanoke circuit.
AEP-2020-AP039 | AEP | PJM West | 2020-09-11 | 2020-11-20 |  |  |  | Kincaid Area Project | APCO Distribution has requested a new distribution station located in Fayette County, West Virginia. Summer projected load: 9 MVA Winter projected load: 14 MVA.
AEP-2020-OH005 | AEP | PJM West | 2020-02-21 | [5 empty] | Holmes-Wayne Electric Cooperative has requested service for a new delivery point near Winesburg, Ohio. • The anticipated new load is 8 MW
AEP-2020-AP040 | AEP | PJM West | 2020-09-11 | 2020-10-16 |  |  |  | Sullivan, TN | Station Station Name: Lovedale Circuit Breakers A, B & G (34.5 KV) Concerns: All of these breakers are 52 years old, oil filled without oil containment; oil filled breakers pose significant environmental risk associated with oil handling and leaks. Additionally, oil filled breakers require frequent maintenance. Oil spills are common and can result in significant environmental mitigation costs. Breakers A & B have experienced 41 & 11 fault operations, respectively, exceeding manufacturer’s recommended number of 10. Breakers A, B & G are 3 of 31 of the FKA-34.5-1500-1 model remaining on the AEP system. Spare parts for these units are impossible to procure as this model type is no longer vendor supported. Other station concerns: The station yard is very cramped and tight. There is limited ability for crews to perform necessary maintenance due to a lack of space for vehicles and equipment. The bus arrangement is tight and congested with tubing comprised mainly of copper Cap and pin insulators are used throughout the station There are additional needs on the Distribution voltage class equipment within the station Relay concerns: Currently, 33 of the 40 deployed relays are electromechanical type which have significant limitations with regards to fault data collection and retention. In addition, these relays lack vendor support with no spare part availability for repairs.
AEP-2020-OH007 | AEP | PJM West | 2020-02-21 | [5 empty] | The Robyville 69-12kV substation is in poor condition. The 69kV breaker ‘C’ is an oil-filled unit from 1965, has experienced 143 fault operations (manufacturer recommends 10), and has mechanical problems on the breaker’s open/close mechanism. • The station consists of deteriorating wooden 69kV & 12kV station structures. Foundations for the 2- transformers and voltage regulator are of wooden rail road tie construction. The station fence and retaining wall are in very poor condition. The two distribution transformers date to 1941 & 1947; both are showing signs of thermal degradation (due to past electrical faults), high carbon-monoxide levels (due to excessive heating), contaminated oil, and hot spots. • The small control house dates to the 1940’s. Of the 16 relays, 12 are original electromechanical models, which lack modern fault recording, no SCADA functionality, and have limited spare part availability.
AEP-2020-AP046 | AEP | PJM West | 2020-11-20 | 2020-12-18 |  |  |  | Scottsville, VA Area | AEP Distribution is requesting additional load serving capability at Scottsville Station 46 kV Circuit Breaker E: 72EPB-31.5-20 Type, SF-6 filled breaker manufactured in 1992 This circuit breaker has experienced 116 fault operations, exceeding the manufacturer’s designed number of 15 full fault operations. Each of these fault operations is likely not at the full fault current rating of the circuit breaker, but with each fault operation of any magnitude comes accelerated aging. Since 2003, there have been 24 gas leak malfunction records associated with CB E at Scottsville These model types have historically exhibited bad gas leaks, bushing failures, and CT cores getting wet.
AEP-2020-IM002 | AEP | PJM West | 2020-02-21 | 2020-07-17 | 2020-10-21 | s2345 |  | Main Street-Riverside 34.5kV Line Rebuild | Main Street-Riverside 34.5kV line: • 4.1 miles of the 4.6 mile 34.5kV line from Main St. –Riverside 34.5kV: • 1930’s double circuit steal lattice towers and 1950’s wood pole line with cross arm construction • 15 structures with at least one open condition (21% of the line) • Open conditions include pole leaning, rot, woodpecker or insect damage Riverside Station: • There are (2) 34.5kV oil filled breakers of FK-type 1960’s vintage • Circuit breaker G has exceeded it’s manufacturer designed number of fault operations • The common failure mode documented by AEP are compressor failures and valve defects which cause low pressure and oil leaks • The manufacturer no longer provides support for this fleet of circuit breakers. Spare parts are not available
AEP-2020-OH010 | AEP | PJM West | 2020-02-21 | [5 empty] | AEP Ohio has requested a new delivery point between Coolville and Elliott Stations. Anticipated peak load is approximately 7.5 MVA that will be transferred from nearby stations in the area.
AEP-2020-IM003 | AEP | PJM West | 2020-02-21 | 2020-12-18 |  |  |  | Niles Area - West | Buchanan Hydro Station: Buchanan Hydro station has flooded twice in the last 5 years causing the 12kV load to be dropped from the station. (2) FK-type Oil filled breakers, AEP has common failure modes for these types of breakers with compressor failures, valve defects, reclose failures and charging motor failures. Both breakers installed in 2003 Breaker A has exceeded the designed number of fault operations (2) CF-Type oil filled breakers. This model family has experienced major malfunctions associated with their hydraulic mechanisms which have led to several failures to close and other types of mis-operations. Both breakers have exceed the designed number of fault operations Transformer #1 was installed in 1964. The transformer has elevated levels of carbon dioxide and ethylene, there is indication of overheating faults occurring in the main tank which have further degraded the insulating paper materials. There is also indication of capacitive layer deterioration. Transformer #2 was installed in 1965. The age of the unit’s insulation materials can lead to susceptibility of short circuit faults which may cause failure in the main tank. The transformer has elevated levels of carbon dioxide and ethylene, there is indication of overheating faults occurring in the main tank which have further degraded the insulating paper materials Buchanan Hydro –Clark Equipment Tap 34.5kV: 1.36 miles of 1954 and 1984 wood pole cross arm line 10 unique structures (26%) with at least one open condition Open conditions include pole or cross arm with rot conditions
AEP-2020-OH012 | AEP | PJM West | 2020-02-21 | [5 empty] | Jefferson-Lick 69 kV line - Original Construction Date: 1927 - Length: 12.5 miles - Original Construction Type: Wood (1927, 1953, and 1980s) - Conductor Type: 8.5 miles of 4/0 ACSR conductor (1927 and 1967) with 4.0 miles of 336 ACSR conductor (1980s) - Outages: 4 Permanent and 17 Momentary (5 years) - 3.96 million customer minutes of interruption (CMI) associated with the Firebrick – Lick 69 kV circuit over the last 5 years. - Conditions: 27 of 93 structures have at least one open condition including rot top pole, crossarm damage, and insulator issues
AEP-2020-IM004 | AEP | PJM West | 2020-02-21 | 2020-05-22 | 2020-08-06 | S2273 |  | Winchester Area Improvements Supplemental | Anchor Hocking – Winchester 69kV Line (~1.25 Miles) • 1968 vintage wood pole, crossarm construction • There are currently 12 open conditions on this line (11 structures with at least one open condition or 25% of the line). • Open conditions include: Damaged pole, worn shield wires, stolen ground lead wires, and damaged jumpers. Anchor Hocking 69kV station • Breaker B 69kV • 1972 vintage oil filled, CF-type breaker. This type is oil filled without oil containment. Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units not possible as these models are no longer vendor supported
AEP-2020-IM005 | AEP | PJM West | 2020-02-21 | 2020-05-22 | 2020-08-06 | S2274 |  | Madison-Pendleton 138kV Line Rebuild | Madison – Pendleton 138kV Line (~4.2 Miles) • 1967 vintage wood pole, H-Frame construction • There are currently 16 open conditions on this line (9 structures with at least one open condition or 24% of the line). • Open conditions include: Rotting or bowed crossarms or poles, broken shield wires, and stolen ground lead wires. Meadowbrook 138/34.5kV station • Three-terminal line and overlapping zones of protection on the bus, line, and transformer.
AEP-2020-IM008 | AEP | PJM West | 2020-02-21 | 2020-11-20 |  |  |  | Bixler Area Improvements | I&M Distribution has requested a expansion of their Bixler station and a rebuild of their North Kendallville stations in order to help address the loading and recoverability of the area. These stations serve sensitive customers, including industrial plants and the local hospital, and the load is not recoverable for an outage due to the radial nature of the transmission feeds as presented in need AEP-2019-IM015
AEP-2020-OH016 | AEP | PJM West | 2020-03-19 | [5 empty] | AEP Ohio has requested a new 138kV delivery point (Poth) off the East Broad Street - Bexley 138kV circuit by December 2022. At Etna Road station, 101/102 of the relays are electro-mechanical that are no longer supported by the manufacturer, lack SCADA ability, and lack fault collection. 46 kV CBs 30, 31, 32, 33, 34, and 36 (vintage 1955) are oil type breakers, with some have a high number of fault operations, and are an obsolete kV. Over the last 5 years we have had 402,323 CMI and three outages. Etna-Groves Road 40 kV line is a majority 1960s vintage (70%) wood pole line with the remainder being built since 1990. The conductor is the original 636 ACSR from 1965. There are a total of 56 open conditions on this line with 51% (42/82) of the poles having at least one condition. These conditions include rot top poles and cross arms, woodpecker damage, broken/missing ground leads, and damaged guy wires. Over the last 5 years there have been 1 momentary and 3 permenant outages on this line. Etna Tap 40 kV extension (part of the Etna Bexley circuit) is a vintage 1957 (57%) with the remainder between 1970 (8%), 1980 (5%), 1990 (5%), and 2010 (22%). There are currently 30 open conditions with 28% (22/80) of poles having at least one condition. These conditions include rot top poles and cross arms, woodpecker damage, broken/missing ground leads, and damaged guy wires. Over the last 5 years there have been 4 momentary and 2 permanent outages.
AEP-2020-OH017 | AEP | PJM West | 2020-03-19 | [5 empty] | Customer Service: • Buckeye Rural Electric Cooperative, Inc. has requested 69kV service to a new delivery point near AEP’s Hemlock station by December 2022. Anticipated load is approximately 2.6 MW of transferred load.
AEP-2020-OH019 | AEP | PJM West | 2020-05-22 | [5 empty] | Customer Service: Timken Richville 138kV Station Peak customer load is 150 MW; steel mill with an arc furnace. Outage history: the customer has experienced 2 prolonged outages over the past 5 years. Any interruption to service is disruptive and costly for this facility. The customer’s sensitive equipment includes a continuous caster, electric arc furnace, and refining furnaces. If there is a loss of power it could lead to the customer having to dump the molten steel and risks the steel solidifying in the equipment. These events would be very detrimental to the company’s long-term business operations. Operational Flexibility & Efficiency: Timken Richville 138kV Station The station contains 2- 138kV lines and 2- 138kV customer feeds with only a single 138kV bus-tie breaker. A fault on either of the 138kV lines or bus will take out up to 75 MW of load for a single event (1/2 of peak load). A fault on either 138kV circuit requires tripping one of the customer’s 138kV breakers to clear the fault. If the customer’s equipment were to fail to clear a line fault, a single 138kV circuit fault would expand to take out both 138kV circuits connected to Timken Richville, dropping the customer entirely and requiring additional remote-end clearing (at South Canton or Timken station). Equipment Material Condition, Performance and Risk: Timken Richville 138kV Station The station was constructed in 1985 and 32 of the 34 protective relays in the station are electromechanical (with 2 static relays). Electromechanical relays lack vendor support, don’t have SCADA, and lack fault data collection. The line protection to Timken and to South Canton consists of an outdated pilot wire scheme that is increasingly prone to failure. The RTU is a legacy model that is no longer supported by the manufacturer. AC station service comes from the customer’s substation, which is a reliability concern. The control house ceiling is made of an asbestos-cement product (transite). There is no fence separating AEP’s substation from the customer’s substation, which is a physical security risk. The metering PT’s and CT’s show signs of heavy rusting.
AEP-2020-OH020 | AEP | PJM West | 2020-03-19 | [5 empty] | East Leipsic Townwood Switch 34.5 kV Line: The East Leipsic Townwood Switch 34.5 kV line (vintage 1934) is 4.04 miles long and still has the original conductor on 65% of the line with the remainder from 1991 (26%) and 2011 (9%). The conductor is a mixture of 336 ACSR (65%), 4/0 ACSR (26%), and 556 ACSR (9%). The majority of the wood pole structures are a mix of 1960s (33%), 1970s (20%), 1990s (36%), and 2000s (11% - steel) vintage. There are 9 open conditions on the 92 structures that include broken/damaged insulators, damaged hardware, and missing ground leads. New Liberty Townwood Switch 34.5 kV Line: The New Libery Townwood Switch 34.5 kV line (vintage 1936) is 13.99 miles long and still has the original conductor on 50% of the line with the remainder from 1939 (49%) and 1956 (1%). The conductor is a mixture of 336 ACSR (50%), 2/0 ACSR (49%) and 4/0 (1%). The majority of the wood pole structures are a mix of 1930s (13%), 1950s (5%), 1960s (14%), 1970s (4%), 1980s (7%), 1990s (27%), 2000s (30%). There are 49 open conditions on this 307 structure circuit that include insect damage, broken ground wire, woodpecker damage, rot heart/top, and loose insulators. There have been a total of 1 momentary and 2 permanent outages over the last 5 years (57,384 CMI) on these two line sections.
AEP-2020-OH021 | AEP | PJM West | 2020-04-20 |  |  |  |  | Putnam/Hancock County | Line Name:Kalida –Rockhill 34.5 kV • Original Install Date (Age): 1923 • Length of Line: 17.22 miles • Total structure count: 451 • Original Line Construction Type: Wood Monopoles • 96% of structures are from 1923, remaining 4% from 2000’s. • Short wood poles susceptible to vegetation outages outside of the ROW. • Wooden Crossarmconstruction with vertical post insulators. • Conductor Type: #1 Copper from 1923 (99%), remaining 795 ACSR (
AEP-2020-OH022 | AEP | PJM West | 2020-02-21 | [5 empty] | Dexter – Rosewood 138kV (1927 Steel Lattice Line) • Length: 8 Miles • Original Construction Type: Aluminum/Steel Lattice • Original Conductor Type: 397.5 CM ACSR 30/7 (1926 vintage) • Momentary/Permanent Outages: 3 total outages over last 5 years • Total structure count: 30 • Please reference needs materials on pre-1930s era lattice lines • There is an additional 2.5 miles of the 1920’s Philo - Rutland lattice line which is de-energized and runs through the middle of The Plains community north of Athens
AEP-2020-OH024 | AEP | PJM West | 2020-04-20 |  |  |  |  | Tuscarawas County, Ohio | Newcomerstown – West New Philadelphia 34.5kV (Install Date 1925) Line Characteristics: • Line Length: 17.5 Miles • Total Structure Count: 382 • Original Construction Type: Wood • Conductor Types: 3/0 Copper (15.13 Miles), 336.4 CM ACSR Merlin (1.21 Miles), & 556.5 CM ACSR Osprey (0.06 Miles) • The majority of the conductors were installed in 1925. • The circuit serves four substations (two retail customers, one AEP distribution, and one rural co-op). Outage History: • Momentary/Permanent Outages and Duration: 6 momentary & 3 Permanent • CMI (Last 5 years): 347,354 minutes Line Conditions: • 99 structures with at least one open condition, 25.9% of the total structures. • 84 structure based conditions: rot heart, siting in water, woodpecker holes, insect damage, split structures, twisted crossarm, and leaning/transverse poles. • 4 damaged conductor conditions. • 11 broken ground lead wire conditions. • 4 hardware based conditions: chipped insulator, missing guy guard, & split bayonet.
AEP-2020-IM009 | AEP | PJM West | 2020-02-21 | 2020-12-18 |  |  |  | Niles Area - West | Bridgman-Pletcher 69kV line: 7.7 miles of 1964 wood pole line 57 unique structures (46%) with at least one open conditions relating to structure and conductor issues Open conditions include rotted poles, burnt or broken insulators, split or damaged poles or broken conductor strands, woodpecker damage and guy/ground wire damage
AEP-2020-OH026 | AEP | PJM West | 2020-04-20 |  |  |  |  | Logan, Ohio | Ralston – North Logan 69 kV • Original Install Date (Age): 1950’s and 1960’s • Length of Line: 15.3 miles • Total structure count: 148 • Original Line Construction Type: Wood • Conductor Type: 336.4 ACSR 30/7 CONDITION / PERFORMANCE / RISK ASSESSMENT: • Momentary/Permanent Outages and Duration: 13 Momentary and 5 permanent Outage • CMI (last 5 years only): 1,496,000 Line Condition Summary: Ralston – North Logan line section: • 84 structures with at least one open condition. • 59 structure related open conditions including broken crossarms, insect damage, rot heart, rot top, split poles and crossarms, and woodpecker holes • 9 open conditions related to the conductor, including broken strands • 7 open conditions related to the shielding wire and grounding, including broken shield wire strands • 30 hardware related open conditions related to insulator, conductor hardware, or shield wire hardware, including broken, burnt, or chipped insulators
AEP-2020-IM013 | AEP | PJM West | 2020-03-19 | 2020-07-17 | 2020-10-21 | s2345 |  | Main Street-Riverside 34.5kV Line Rebuild | Riverside Station: (2) 138kV Breakers O & A - 1988 vintage SF-6 filled breakers - The breaker type has hydraulic leak issues on internal mechanisms which are caused by porous cylinder blocks and chips in the seal groove on the spring connecting rods. - Breaker A has operated for a fault 17 times exceeding its manufacturer recommendation of fault operations (10) -
AEP-2020-OH028 | AEP | PJM West | 2020-07-17 |  |  |  |  | Malta , Ohio | West Malta 69kV Circuit Breaker “A” 1965 • Interrupting Medium: Oil • Additional Information: – Interrupting Capability: 21 kA – Oil breaker maintenance has become more difficult due to the oil handling required to maintain them. Oil spills are frequent with breaker failures and routine maintenance and can become an environmental hazard. Spare parts for these units are not available due to their obsoleteness. Additional Information: • MOAB X has a retrofitted motor mechanism installed that prohibits the switch from opening correctly. • Overlapping zone of protection exist at the station between a 69 kV line, the bus, and the 69/12 kV transformer which can result in relay coordination issues. • 23 of the 25 relays at the station are of the electromechanical type and 2 of the static type all of which have significant limitations with regards to fault data collection and retention. In addition, these no longer have vendor support and spare parts are unavailable.
AEP-2020-OH029 | AEP | PJM West | 2020-06-19 |  |  |  |  | Tuscarawas & Carroll County Ohio | East Dover Carroll Co-op 69kV (15.30 miles) The line consist of wooden monopoles, H-frames and 3 pole structures. The line was originally built in 1958 with 4/0 ACSR conductor. There are currently 95 structures (55.5% of the line) with at least one open condition. 69 structure with open conditions consisting of insect damage, rot top, rot heart, split crossarms, broken knee brace, rot shell, split poles and woodpecker holes. 7 conductor based open conditions consisting of damaged conductors and malfunctioning splices. 28 hardware based open conditions consisting of loose/broken insulators, burnt insulators, insulators missing bolts and broken/damaged/missing molding. For the 2015-2020 time period there have been 13 outage events on the Carrolton – East Dover Circuit. The permanent outages resulted in 2,344,426 minutes of interruption to the 2,643 customers served from the circuit (all Carroll Electric Co-op).
AEP-2020-IM014 | AEP | PJM West | 2020-05-22 | 2020-11-20 |  |  |  | Eastern Melita Area Improvements | Anthony 138/34.5/12kV Station 34.5/12kV Transformer #4 is a 1954 unit Increased CO and CO2 gassing with decreasing interfacial tension and oil deterioration 138/34.5kV Transformer #5 currently has a high side MOAB switch protection scheme Filtration 34.5/12kV Switch Station I&M has an obligation to remove this station upon completion of the City of Fort Wayne tunneling project Lincoln – Harvest Park 34.5kV line (~1.5 miles) 1.5 miles of 1920-1930’s steel structures with 300,000 CM copper conductor and 3#8 copperweld shield-wire Field inspection found the 10 1920’s towers had significant rusting Older copper wires like the 300,000 CM copper conductor and the3#8 copperweld shield wire have a higher rate of failure and become brittle and difficult to splice with age. 3 structures had flashover damage and 4 structures had severe rust and corrosion on the insulation. Lincoln – Anthony 34.5kV line (~1.1 miles) 1.1 miles of 1971 wood pole line with 300,000 CM copper conductor This line segment fails to meet NESC loading criteria. This line segment fails to meet AEP loading and leakage distance requirements This line segment fails to meet ASCE strength requirements. 4 poles have crossarm decay, 2 poles have splitting or decay, 1 broken static lead and 1 knee brace with decay across 21 poles on the line. Lincoln – Anthony 138/34.5kV line (~3.07 miles) 3.07 miles of 1971 wood pole line 20 unique structures with open conditions (31% of the line). These conditions include insect damaged poles, twisted crossarms, broken strands and missing grounds. This line segment fails to meet AEP strength and leakage distance requirements. The line segment fails to meet NESC loading criteria The line segment fails to meet ASCE strength requirements 4 poles have flashover indication, 1 broken static lead and 1 pole vertically splitting
AEP-2020-IM015 | AEP | PJM West | 2020-04-20 | 2020-07-17 | 2020-10-21 | s2344 |  | Colony Bay – Melita 69kV Line Rebuild | Colony Bay – Melita 69kV (5.8 miles) • The Colony Bay – Melita circuit has ~5.8 miles of primarily 1960 wood pole structures • This section has 34 open conditions across 26 unique poles (~17% of line). These conditions include, but aren’t limited to Stolen/broken ground leads, broken insulators, damaged and rotting poles. • An additional 23 poles on this section (~15%) were found to be decayed to the point of failure. These poles had steel reinforcersinstalled to allow them to last until a more permanent fix was available. • The 2014-2019 5 year period this line was subject to 3 momentary outages and 3 permanent outages. Hadley 69kV station • Station has a bus tie switch that breakers the bus differential. AEP has been addressing these as we have the opportunity
AEP-2020-OH032 | AEP | PJM West | 2020-05-22 | [5 empty] | East Beaver 138/69 kV Transformer #1: The 138/69 kV 56/72 MVA (vintage 1962) at East Beaver has failed. There is no spare on site to utilize as a replacement.
AEP-2020-OH033 | AEP | PJM West | 2020-05-22 | [5 empty] | Vine Station Vine station is located in the heart of the downtown Columbus Arena District. The downtown area of Columbus has experienced a significant level of growth and development over the last decade. Projects such as the recently announced MLS Crew stadium indicates continued growth for the foreseeable future. The footprint of the existing station is extremely small, which creates issues when performing routine maintenance, severely limits the ability to replace major equipment, and often results in extended outages due to clearance issues. These space constrains also limit the ability to expand the station to accommodate future load growth. A mobile cannot fit inside the station; any mobile installs require placing it in the street and constructing temporary facilities to connect it. Circuit Breakers 101, 102, 103, 104, 106, 107 138 kV 2000A 40kA* oil type breakers (*CB 107 is a 50kA) Install date ranging from 1974 -1977 (43-46 years old) Oil breakers that are difficult to maintain due to the required oil handling requirements. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. Other needs include damage to bushings, lack of spare part availability, and lack of vendor support of the breakers. Capacitor Switcher EE 138 kV Mark V type switcher MARK V models have a history of malfunctioning and has presented AEP with a large # of failures and mis-operations including catastrophic equipment failures involving failure to trip. Gay – Vine 138 kV Underground Circuit* The existing Gay – Vine 138 kV underground circuit is approximately 1.4 miles long and was originally installed in the 1960’s. Hess – Vine 138 kV Underground Circuit* The existing Hess – Vine 138 kV underground circuit is approximately 2.5 miles long and was originally installed in the 1980’s. Italian Village – Vine 138 kV Underground Circuit* The existing Italian Village – Vine 138 kV underground circuit is approximately 1.3 miles long and was originally installed in the 1990’s. *All of these circuits utilize an underground oil-filled pipe type cable design. Oil-filled pipe type underground cables come with several challenges/risks in densely populated urban areas. There is a single manufacturer of oil-filled cables which has informed AEP of its desire to discontinue this product due to lack of demand and cheaper available alternates such as XLPE. A failure of any section may result in weeks of outage to customers in downtown Columbus.
AEP-2020-OH034 | AEP | PJM West | 2020-06-19 |  |  |  |  | Mansfield Ohio | Line Philo – Howard 138kV (vintage 1929): The Philo –Howard 138 kV line serves 60 MVA of load consisting of four AEP substations and three non-AEP substations. LINE CHARACTERISTICS Length of Line: 81.15 Miles Original install date: 1929 Total structure count: 404, 398 dating back to original installation. Conductor Type: 556,500 CM ACSR 18/1 (Osprey) and 556,500 CM ACSR 26/7 (Dove) CONDITION / PERFORMANCE / RISK ASSESSMENT: Momentary/Permanent Outages and Duration: 35 total outages: 28 (Momentary), 7 (Permanent). 5 Year CMI: 2,667,652 Number of open Structure, Conductor, and Hardware conditions: 149 Conditions include broken conductor strands, burnt insulators, along with broken/damaged lattice members and hardware. Structures with at least one open condition: 55 The line does not meet current grounding and shielding requirements, due to the condition of the obsolete shield wire size (159 ACSR), and the line shielding angle being inadequate. This T-line exhibits similar conditions as the examples listed in AEP’s pre-1930’s steel lattice tower line presentation.
AEP-2020-IM016 | AEP | PJM West | 2020-04-20 | 2020-09-11 | 2021-01-13 | s2392 |  | Rob Park – Lincoln 138kV line rebuild | Robison Park – Lincoln 138kV (~10.9 7.8 mi) 44 structures with an open condition (~67%) with most revolving around rusted legs, broken/chipped insulators and rusted shield wire Fails to meet current AEP structural strength requirements Fails to meet AEP shield angle requirements Top half of towers were replaced and re-conductored in 1968 to allow for 138kV voltage operation, but the bottom half and foundations are original 1928 installation 4 MOABS in series currently which is over the AEP max of 3. Note: the remaining 3.1 miles of line is covered under need AEP-2019-IM038 and will be addressed with a future solution.
AEP-2020-IM017 | AEP | PJM West | 2020-05-12 | 2020-09-01 | 2021-01-13 | s2390 |  | DC Cook Breaker Failure | DC Cook 765/345 Station 345kV CB N1 Failure The 345kV CB failed internally on phase 2 in March 2020 The DC Cook 345kV CB N1 is an HVB362 type SF6 breaker Manufactured in 2002 Breaker N1 had 2 fault interruptions since install date of 2003
AEP-2020-OH037 | AEP | PJM West | 2020-10-16 |  |  |  |  | East Lima – Columbus Grove 69kV Line Rebuild | East Lima – Columbus Grove 69kV (vintage 1953) Original install date: 1953 Length of Line: 10.86 miles Total structure count: 255; 150 dating back to original installation. Original Line Construction Type: Wood monopoles Cross Arm Material: Wood The line has vertical and horizontal ceramic insulators and is butt wrap grounded Conductor: 4/0 ACSR 6/1 (Penguin) -72% and 556 kCM ACSR 26/7 (Dove) -28% Momentary/Permanent Outages and Duration: 20 total outages: 17 (Momentary), 3 (Permanent) 5 Year CMI: 911,294 Number of open conditions: 112 Open conditions on 94 unique structures Open conditions include: rotten heart, woodpecker holes, insect damage, split crossarms, burnt insulators, and broken ground lead wires Risk Number of Customers at Risk: 3,272 Load at Risk: 22.71 MVA The grounding/shielding and the insulation of the line is inadequate according to the current AEP standards.
AEP-2020-OH038 | AEP | PJM West | 2020-08-14 |  |  |  |  | Columbus, OH | Customer Service: The customer served out of Buckeye Steel station has indicated they no longer require Transmission service and has disconnected their load. Equipment Material/Condition/Performance/Risk: The oil filled circuit breakers 101 – 104 (vintage 1977) have a number of malfunctions/maintenance issues including hydraulic oil leaks, replaced hydraulic pressure system motors and pumps. Breaker 103 has experienced 12 fault operations, exceeding the manufacturer recommend number of 10. Additionally, oil filled breakers require frequent maintenance. Oil spills are common and can result in significant environmental mitigation costs. 37 of the 41 relays are electromechanical type relays, which have no vendor support due to their obsoleteness, lack SCADA ability, and don’t have fault data collection capabilities. The existing legacy RTU is no longer supported by the vendor and has no spare parts available.
AEP-2020-OH039 | AEP | PJM West | 2020-10-16 |  |  |  |  | Benwood 69kV | Benwood 69kV 69 kV oil filled circuit breakers “A” & “B” have 61 and 39 fault operations respectively (vintage 1965). They both have exceeded the recommended fault operations of 10. The breakers do not have oil containment. ‘FK’ model breakers, which are prone to compressor failures, valve defects, and oil contamination Control cables are direct-buried, not housed in conduit, which presents a greater risk of failure Oil filled breakers require frequent maintenance. Oil spills are common and can result in significant environmental mitigation costs. 22 out 23 relays in service at the station are electromechanical and 1 is a static relay. All of these relays have no vendor support, SCADA functionality, or spare parts available for repairs The EMC relays lack fault recording and retention capabilities. 69kV bus protection is a legacy design, with no redundancy The 69kV circuit protection systems to Brues & Moundsville stations use a legacy pilot wire system; the pilot wire to Moundsville is not functional (requiring backup system protection) The 300MCM bare Copper bus conductor is showing degradation 69kV bus PT’s are original to the station and of an obsolete design, along with the station service The fence perimeter is too close to the station equipment. Station fencing is not up to AEP standard and has animal concerns which can lead to outages at the station. The control house has past flooding damage, asbestos, and lead paint concerns. The control house has outdated and rusted AC/DC cabinets.
AEP-2020-IM019 | AEP | PJM West | 2020-09-11 | 2021-02-17 |  |  |  | Muncie, Indiana | Wes Del 138/12kv station 138/69/12 kV Transformer #1 Unit failed in February 2020, station currently served by mobile unit 1968 vintage Line MOABs X & Y Configuration of switches on non-standard structure makes them impossible to maintain without a transformer outage. Due to switch operating condition and length of operating pipe, motor operators cannot be properly adjusted to attain full open/close position. Switches were manufactured in 1969 Neither switch will fully close after operation without assistance.
AEP-2020-OH041 | AEP | PJM West | 2020-10-16 |  |  |  |  | Astor – East Broad Street 138 kV | Astor – East Broad Street 138 kV Single Circuit ( 2.75 miles) From 2015 – 2020 this circuit has experienced 2 momentary and 4 permanent outages resulting in 671K CMI. The circuit currently has 54 open conditions on 30 structures ( out of 55 total structures) which includes pole damage, rot top, rotted/spit poles, and missing ground lead wires. 12 structures have been replaced at different times from 1970 to 2011; remaining are wood poles from 1955. The circuit conductor span was primarily installed in 1974 of 636,000 CM ALUM/1350 37 (Orchid 2.75 miles). There are also two spans of 795,000 CM ACSR/AW 26/7 (Drake) An Engineering and Field Assessment was conducted in 2019 and found the following issues: The majority of structures do not meet 2017 NESC Grade B loading criteria The majority of structures do not meet the current AEP structural strength The majority of structures do not meet the current ASCE structural strength requirements The phase to ground clearance of the typical structure supporting the average span length fails to meet current clearance requirements
AEP-2020-OH042 | AEP | PJM West | 2020-10-16 |  |  |  |  | Tiltonsville, Ohio | Three 69 kV circuit breakers CB-H, CB-E, & CB-F are GE ‘FK’ oil filled breakers of 1950s and 1970s vintage without oil containment and two of them have exceeded the recommended fault operations of 10. CB-H has 16 fault operations and CB-F 12 has fault operations. Additionally, oil filled breakers require frequent maintenance. Oil spills are common and can result in significant environmental mitigation costs. The 138/69kV, 90 MVA transformer is a 1978 vintage with decomposition of the paper insulating materials, signs of faults inside the tank, a dielectric breakdown. In addition, the transformer lacks oil containment system and sits on wood railroad ties. Currently, 57 of the 63 relays (90% of all station relays) are in need of replacement. 55 are of the electromechanical type and 2 of the static type, none of which have spare parts available for repairs or vendor support, lack fault data collection ability, and don’t allow for SCADA functionality. Over the last 5 years there have been 1.8 million minutes of CMI at the station, which included 6 outage events due to equipment failure. The transformer protection includes an obsolete MOAB-ground-switch system, which relies on remote station fault clearing (at West Bellaire and FE’s Windsor station). The lack of sectionalizing at the station creates dissimilar zones of protection (line, bus, and transformer), which can cause over tripping and miss-operations. This station (vintage 1935) has numerous other issues of concern: station service, lead paint, control house, numerous disconnect switches, cap-and-pin insulators prone to failure, battery system, bus PT’s, crumbling foundations, inadequate grounding, presence of PCB’s, and many direct-bury cables past their expected lifespan.
AEP-2020-OH043 | AEP | PJM West | 2020-10-16 |  |  |  |  | Ross County, Ohio | Slate Mills Station (vintage 1973) A recent inspection of Slate Mills Station (69/12 kV) has revealed significant deterioration of the wood poles that make up the majority of the station’s structures. Concerns for the long term structural integrity of the station have led to the facility being classified as an imminent failure with short term and long term mitigation measures being actively investigated. Other equipment within the station is also showing signs of deterioration including the arrestors, bus work, and cross arms. AEP Ohio does not have the ability to transfer all of the customers served from Slate Mills elsewhere in the event of a failure at the station.
AEP-2020-OH044 | AEP | PJM West | 2020-10-16 |  |  |  |  | Van Wert County, Ohio | Line Name: Ohio City – West Van Wert 34.5kV Circuit LINE CHARACTERISTICS Original Install Date (Age): 1963 (57 years) Length of Line: 8.90 miles Total structure count: 173 Original Line Construction Type: Wood 62% of structures replaced in 1994. Conductor Type: 1/0 Copper 7 (1939 Install), 4/0 ACSR 6/1 Penguin (1966 Install) CONDITION / PERFORMANCE / RISK ASSESSMENT: Condition Summary Open conditions / defects / inspection failures include: missing/broken ground wires, woodpecker damage, broken guy wires Number of structures with defects/inspection failures: 24 Load at Risk: 3.997 MVA CMI: 127,978 Customer Minutes of Interruption CONDITION / PERFORMANCE / RISK ASSESSMENT: Station Name: Ohio City Transformers Concerns: 1951 vintage and shows significant signs of dielectric breakdown (paper insulation), accessory damage (likely sludge in radiators, core, and coil), and short circuit breakdown. OPERATIONAL EFFICIENCY: AEP has a normally open 34.5 kV tie with Dayton at Dayton’s Rockford Substation that is built to 69kV standards. This is an out of phase interconnection point and can only be closed if the 12kV Dayton Rockford bus is de-energized first and the line is energized from AEP. AEP’s Ohio City station is a radially served load out of West Van Wert. Since this is a normally open point, the Rockford load is radial under most operating conditions since a manual process must take place to switch the load to AEP’s source if there is an issue with the Celina-Coldwater-Rockford 6688 69kV line. Dayton has limited switching options from Rockford substation so, the normally open point has needed to be used multiple times in recent years to transfer customers to the Ohio City source due to outages on the Dayton system.
AEP-2020-OH045 | AEP | PJM West | 2020-11-20 |  |  |  |  | Columbus, Ohio | • AEP Ohio has requested installation of a second 138/13.8 kV transformer at Fifth Ave Station to address increased loading on the existing distribution feeders at the station due to load growth in the area. Fifth Avenue station has limited transferability and serves approximately 7,000 customers via a single transformer in an urban environment. • AEP Ohio has also expressed concerns over the amount of exposure that existing feeders out of Hess station are subject to in the area.
AEP-2020-OH046 | AEP | PJM West | 2020-12-18 |  |  |  |  | Allen County, Ohio | Customer Service: Station/Area Name: Bluelick Switch 34.5 kV. Load: 3.185MW Existing/3.7MW projected by 2029. Customer Request: The customer has requested to upgrade their existing delivery point from 34.5 kV to 69 kV. Requested In-service Date: 6/1/2024.
AEP-2020-OH001 | AEP | PJM West | 2020-03-19 | 2021-02-17 |  |  |  | Muskingum, Guernsey, Tuscarawas Counties, Ohio | The Philo-Newcomerstown 138kV transmission line section is 32 miles long and consists of portions of the following circuits: Philo-South Canton (32 miles of the total circuit length of 75.2 miles). The line was originally built in 1942 with steel lattice towers. The conductor is 6-wired single-circuit, with one side installed in 1942 (397 ACSR) and the other side installed in 1954 (477 ACSR). The line does not meet current grounding and shielding requirements, due to the condition of the obsolete shield wire size (159 ACSR), and the line shielding angle being inadequate. This T-line exhibits similar conditions as the examples listed in AEP’s 1930’s steel lattice tower line presentation. The Philo-South Canton 138kV circuit has experienced 18 momentary outages over the past 5 years and 4 sustained outages, resulting in 437,567 minutes of CMI. There are currently 18 open conditions on the circuit. Examples of the conditions include: burnt insulators, worn hardware, rusting towers, damaged shield wire, and severe rusting of the tower steel. The Philo-Newcomerstown 138kV circuit contains 3 consecutive hard taps: Chandlersville Co-op, Bridgeville, Bethel Church Co-op. Without line sectionalizing switches at these taps, it makes it very difficult to perform T-Line maintenance and restoration activities. Outages must be scheduled with the customers at each of these stations whenever the 138kV circuit needs taken out of service.
AEP-2020-OH048 | AEP | PJM West | 2020-12-18 |  |  |  |  | Licking County, OH | Customer Service: A customer has requested transmission service at a site just south of the existing Conesville – Corridor 345 kV circuit in New Albany, OH. The customer has indicated an initial peak demand of 64 MW with an ultimate capacity of up to 256 MW at the site.
AEP-2020-OH049 | AEP | PJM West | 2020-12-18 |  |  |  |  | Westfall Delivery Point (SCP) 138kV: Buckeye Power Inc., on behalf of South Central Power Company, has requested transmission service in Wayne Township, Pickaway County, Ohio. SCP currently has a radial 69 kV line served out of AEP’s West Lancaster Station with a load of approximately 42.5 MW in 2022 and growth at a rate of 2% per year. South Central Power Company would like a new transmission delivery point on the on the other end of this long 69 kV radial line (44 miles of exposure; 5 delivery points). Service is requested by March 2022. | Westfall Delivery Point (SCP) 138kV: Buckeye Power Inc., on behalf of South Central Power Company, has requested transmission service in Wayne Township, Pickaway County, Ohio. SCP currently has a radial 69 kV line served out of AEP’s West Lancaster Station with a load of approximately 42.5 MW in 2022 and growth at a rate of 2% per year. South Central Power Company would like a new transmission delivery point on the on the other end of this long 69 kV radial line (44 miles of exposure; 5 delivery points). Service is requested by March 2022.
AEP-2020-OH050 | AEP | PJM West | 2020-03-19 |  |  |  |  | Tuscarawas & Stark Counties, Ohio | The Newcomerstown-Sunnyside eastern 138kV transmission line is 42 miles long, originally constructed in 1923. The vast majority of the structures are still original, as well as the six-wired 336 ACSR conductor, insulators, and hardware. This line is made up of several circuits connected between Newcomerstown and Sunnyside stations. Insulator assemblies are showing corrosion and deterioration, which could lead to additional failures and safety concerns. There have been 0.7 million customer-minutes-of-interruption (CMI) over the 2008-2018 time period. This line has experienced 36 momentary outages and 5 sustained outages over the past 10 years. The Newcomerstown-Torrey western 138kV transmission line is 38.6 miles long and consists of portions of the following circuits: Philo-South Canton (36 miles of the total circuit length of 75.2 miles), South Canton-Timken Richville (2.0 of 3.5 miles), and Timken Richville-Timken (0.6 of 3.4 miles). The line was originally built in 1942 with steel lattice towers. The conductor is 6-wired single-circuit, with one side installed in 1942 (397 ACSR) and the other side installed in 1954 (477 ACSR). The line does not meet current grounding and shielding requirements, due to the condition of the obsolete shield wire size (159 ACSR), and the line shielding angle being inadequate. This T-line exhibits similar conditions as the examples listed in AEP’s 1930’s steel lattice tower line presentation. The Philo-South Canton 138kV circuit has experienced 18 momentary outages over the past 5 years and 4 sustained outages, resulting in 437,567 minutes of CMI. There are currently 18 open conditions on the circuit. Examples of the conditions include: burnt insulators, worn hardware, rusting towers, damaged shield wire, and severe rusting of the tower steel. In addition, the West Dover 138-69kV station creates a 3-terminal point on the line, due to the lack of 138kV line breakers or a 138kV transformer protection device (just a MOAB/ground- switch system today). This complicates the circuit protection scheme and is a risk for misoperations and over-tripping. In addition, due to the lack of breakers at the station, there are 3 dissimilar zones of protection combined: 138kV circuit, 138-69kV XFMR, 69kV bus.
AEP-2021-AP001 | AEP | PJM West | 2021-01-15 |  |  |  |  | Troutville, VA Area | Cloverdale Station: 345/138 kV Transformer #11A: Transformer 11A was manufactured in 1972 with identified upward trending insulation power factor which indicates increased particles in the oil as well as elevated levels of ethylene indicating increased decomposition of the insulating paper materials, decreasing the units ability to withstand electrical faults. Unit leaks oil. Connected in parallel with transformer 11B; high-side connected directly to 345 kV bus #1 exposing it to faults and scheduled maintenance outages. 345/138 kV Transformer #11B: Transformer 11B was manufactured in 1997 with increased tertiary bushing power factor indicating capacitive layer deterioration. The change in bushing dielectric data indicates the tertiary bushings are at greater risk of failure or loss of service of the transformer. Also, observed elevated levels of carbon monoxide and carbon dioxide indicates decomposition of the paper insulation that impairs the units ability to withstand future short circuit or through fault events. Unit leaks oil. Connected in parallel with transformer 11A; high-side connected directly to 345 kV bus #1 exposing it to faults and scheduled maintenance outages. 345/138 kV Transformer #3: High-side connected to 345 kV bus #2 via Motor Operated Air-Break Switch (MOAB) exposing the bus to momentary transformer fault events. 31 of the 94 microprocessor relays in the Cloverdale 138 kV Station utilize obsolete firmware. 69 kV hook-stick circuit breaker and switcher disconnect switches identified in need of replacement with Gang Operated Air-Breaker Switches (GOAB)
AEP-2021-AP002 | AEP | PJM West | 2021-01-15 |  |  |  |  | Buchanan County, Virginia | Line Name: Dismal River – Grundy – Looney Creek 69kV, Original Install Date (Age): 1935, Length of Line: ~8.8 mi , Total structure count: 64, Original Line Construction Type: Wood, Conductor Type: 3/0 ACSR, 336,400 ACSR, 556,500 ACSR, 795,000 ACSR, Momentary/Permanent Outages and Duration: 6 Momentary and 1 permanent Outage, CMI (last 5 years only): 339,660 minutes. Line conditions: 13 structures with at least one open condition, 20% of the structures on this circuit. 16 structure related open conditions: woodpecker holes in poles, rot top crossarms, rot top poles, and a broken knee / vee brace. 1 open condition related to broken guy wire. 13 of 64 structures are 1930s vintage, 20% of the structures on this circuit. 18 of 64 structures are 1970s vintage, 28% of the structures on this circuit. Twenty Mile Switch Station creates a three terminal line with no ability to sectionalize.
AEP-2021-AP003 | AEP | PJM West | 2021-01-15 |  |  |  |  | Smyth County, VA | APCo Distribution has requested a new station to be served from the Broadford — Richlands 138 KV line. The projected peak demand is 21 MW.
AEP-2021-AP004 | AEP | PJM West | 2021-01-15 |  |  |  |  | Smyth/Tazewell County, VA | Line: Saltville — Tazewell 138 KV (installed in 1927). Length: ~21 Miles. Original Construction Type: Lattice Steel. Original Conductor Type: 97.3% 397.5 ACSR, 1 % 795 ACSR, 1.5% 1033.5 ACSR. Momentary/Permanent Outages: 15/2 (5 years). Total structure count: 98. Number of open conditions: 26. Open conditions include: broken conductor strands, broken/burnt insulators. Unique structure count with open conditions: 12 (12%). Additional Info on Insulator & Hardware Corrosion: Section Loss: The connecting elements including the tower attachment hole and the insulator hook have experienced serious cross-section loss due to corrosion and wear. This loss of metal cross-section significantly reduces the capacity of the connection. Corrosion: The insulator caps and connecting hardware have experienced heavy to complete loss of galvanizing. When the protective galvanized coating is gone or significantly compromised, the bare steel corrodes at an accelerated rate. Tower members with corrosion and damage. Lattice tower structures have little structural redundancy. A failure of one member of the structure will impact the integrity of the structure and may cause the entire tower to collapse.
AEP-2021-OH001 | AEP | PJM West | 2021-01-15 |  |  |  |  | Canton, Ohio | Equipment Material/Condition/Performance/Risk: The Wagenhals 138-69-23kV station was originally constructed in 1943. The station directly serves approximately 140 MW of industrial load (130 MW steel mill at 138kV; 10 MW casting plant at 23kV). The 138-23kV transformer #1 (vintage 1957) has the following asset concerns: insulation breakdown, elevated levels of CO2, high moisture readings, leaks, and wood-tie foundations in poor condition. The 138-69-23kV transformer #2 (vintage 1967) has the following asset concerns: insulation breakdown, elevated ethane and ethylene levels, high moisture readings, and low dielectric strength, and wood-tie foundations in poor condition. The control house has various issues: water intrusion, animal-related damage, lead paint, leaking roof, and asbestos. The 23kV yard has corroded steel and crumbling foundations, along with cap-and-pin insulators. In addition, energized equipment does not meet current clearance requirements. There are environmental concerns: positive tests for PCB’s; lead paint and asbestos, which are a safety risk to field personnel. The ground grid is inadequate and the AC station service and DC cabinets are in very poor condition. All 3 station transformers lack an oil containment system. 138kV breaker ‘H’ has routine SF6 leaks and 138kV breaker ‘A’ has an oil leak. There are 3- 69kV oil-filled breakers (P, Q, S), installed between 1962-1970, that are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling requirements. In addition, spare parts or technical support for these breakers are not available. This model of breakers has been prone to hydraulic mechanism malfunctions. The 2- 23kV breakers are oil-filled and were installed in 1977. These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. In addition, spare parts or technical support for these breakers are not available. This model of breakers has been prone to hydraulic mechanism malfunctions. There are a large number of 69kV and 23kV transmission hook-stick switches identified in need of replacement with Gang Operated Air-Breaker Switches (GOAB) . The 138kV & 23kV PT’s are original to the station (1943) and have significant rusting and are at risk of oil spills. The station contains 103 electromechanical relays and 1 static relay. These relays have significant limitations with regard to spare part availability, SCADA functionality, and fault data collection and retention. In addition, these relays lack vendor support. The relays of concern are involved with 138kV, 69kV, & 23kV circuit protection, 69kV & 23kV bus protection, and transformer protection….Operational Flexibility and Efficiency: The 3- transformers lack a high-side fault interrupting devices and require tripping an entire 138kV bus to clear a fault. These dissimilar zones of protection can cause over tripping and mis-operations. The 138kV design consists of 2- straight buses with a single bus-tie breaker, this configuration causes extended outages for maintenance, especially for a station serving a major steel customer. A stuck-breaker contingency on the 138kV bus-tie breaker requires tripping 9- 138kV breakers, 4- 69kV breakers, and 2- 23kV breakers (15 total breakers), taking the entire station out of service. This contingency would result in load loss of approximately 140 MW, loss of a 138kV cap bank, plus the loss of 2 sources to the local 69kV system.
AEP-2021-OH002 | AEP | PJM West | 2021-01-15 |  |  |  |  | Franklin County, OH | Customer Service: A customer has requested transmission service just south of AEP’s existing Parsons Station in Lockbourne, OH. The customer has indicated an initial peak demand of 100 MW with an ultimate capacity of up to 675 MW at the site.
AEP-2020-OH002 | AEP | PJM West | 2020-01-17 | 2020-07-17 | 2020-10-21 | s2343 |  | Salerno 138kV | AEP Ohio is requesting a new 138kV delivery point on the Academia – North Lexington 138 kV circuit by May 2023. Anticipated load is approximately 15 MVA.
AEP-2020-OH004 | AEP | PJM West | 2020-02-21 | 2020-03-19 | 2020-05-11 | S2223 |  | Crooksville-Philo 138 kV Circuit Rebuild | Crooksville –Philo 138kV • Length: 13 Miles • Original Construction Type: Aluminum/Steel Lattice • Original Conductor Type: 397.5 ACSR Lark / 636 ACSR Grosbeak (vintage 1926) • Momentary/Permanent Outages: 1 total outages • CMI: 320,767 • Number of open conditions: 5 • Total structure count: 65 • Open conditions include: Burnt insulators, damaged shield wire • Please reference assumptions materials on pre-1930s era lattice lines
AEP-2020-OH006 | AEP | PJM West | 2020-02-21 | 2020-10-16 |  |  |  | Stockport, Ohio | AEP Ohio is requesting a new 69kV delivery point on the Muskingum River – South Rokeby SW 69kV Circuit. Anticipated load is about 5 MVA
AEP-2020-OH008 | AEP | PJM West | 2020-02-21 | 2020-09-11 | 2021-01-13 | s2393.1-.5 |  | Rob Park – S. Hicksville 69kV line rebuild | Rob Park – South Hicksville (OH) 34kV (~4.6 Miles) • 1956 & 1962 vintage wood pole construction with 32 open conditions on 17 unique structures, approximately 17% of the line. These conditions include but not limited to damaged poles, broken insulators, broken shield wire, rot top and broken Knee/Vee braces • The circuits on this line have had the following outages across the last 5 years. Rob Park – South Hicksville: 9 momentary and 6 permanent CMI: 526,269 North Hicksville – Butler: 5 Momentary and 2 Permanent. CMI: 120 over the last 5 years. • Related to previously shared need AEP-2019-IM014
AEP-2020-OH009 | AEP | PJM West | 2020-02-21 | 2020-08-14 | 2020-10-21 | s2352 |  | Lima Pumping Extension Rebuild | Equipment Material/Condition/Performance/Risk: • This line consists of 15 wood pole structures and has predominantly the original #2 ACSR/AW Sparrow conductors installed in 1943. 9 out of the 15 structures on this line were installed more than 60 years ago. 5 year CMI on this circuit is approximately 95,000. The existing construction is obsolete crossarm construction with 35 kV vertical stud post insulators. Operational Flexibility and Efficiency • The line has experienced four (4) conductor failures since August 1, 2018. The first 8 spans of the line have 35 total splices. During these failures the 34 kV conductors end up falling into and faulting the AEP Ohio 3-phase distribution underbuild, interrupting several hundred additional distribution customers. Customer Service: • Both customers on this radial line experienced multiple outages due to geese contact on AEP’s 34.5 kV transmission line. Additionally these two customers are connected via a hard tap at the end of the radial 34.5 kV line forcing both of them to be out when one of them requests an outage.
APS-2019-015 | APS | PJM West | 2019-12-18 |  |  |  |  | Karns City – Butler 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2019-015 ¦ Karns City – Butler 138 kV Line ¦ 141/179 ¦ 160/192 ¦ Substation Conductor ¦
APS-2020-001 | APS | PJM West | 2020-04-20 |  |  |  |  | Allenport – Frazier 138 kV Line ¦ Frazier – Layton Junction 138 kV Line ¦ Yukon – Smithton Tap 138 kV Line ¦ Smithton Tap – Layton Junction 138 kV Line ¦ Iron Bridge – Layton Junction 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2020-001 ¦ Allenport – Frazier 138 kV Line¦ 225/295¦ 283/349¦ Substation Conductor, Line Trap¦ Frazier – Layton Junction 138 kV Line¦ 283/349¦ 283/349¦ N/A ¦ Yukon – Smithton Tap 138 kV Line¦ 234/287¦ 234/297¦ Line Relaying, Line Trap¦ Smithton Tap – Layton Junction 138 kV Line¦ 234/297¦ 234/297¦ N/A¦ Iron Bridge – Layton Junction 138 kV Line¦ 225/287¦ 258/323¦ Line Relaying, Substation Conductor, Line Trap, CTs
AEP-2020-OH011 | AEP | PJM West | 2020-02-21 | 2020-03-19 | 2020-05-11 | S2224 |  | Athens Area Improvement | Dexter – Rosewood 138kV (1927 Steel Lattice Line) • Length: 8.8 Miles • Original Construction Type: Aluminum/Steel Lattice • Original Conductor Type: 397.5 CM ACSR 30/7 (1926 vintage) • Momentary/Permanent Outages: 3 total outages over last 5 years • Total structure count: 38 • Please reference needs materials on pre-1930s era lattice lines • There is an additional 2.5 miles of the 1920’s Philo - Rutland lattice line which is de-energized and runs through the middle of The Plains community north of Athens
APS-2020-003 | APS | PJM West | 2020-04-22 |  |  |  |  | Burma – Piney 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2020-003 ¦ Burma – Piney 115 kV Line¦ 244/277 ¦ 257/313 ¦ Line Trap, Substation Conductor, Circuit Breaker¦
AEP-2021-AP001 | AEP | PJM West | 2021-01-06 |  |  |  |  | Troutville, VA Area | Cloverdale Station: 345/138 kV Transformer #11A Transformer 11A was manufactured in 1972 with identified upward trending insulation power factor which indicates increased particles in the oil as well as elevated levels of ethylene indicating increased decomposition of the insulating paper materials, decreasing the units ability to withstand electrical faults Unit leaks oil Connected in parallel with transformer 11B; high-side connected directly to 345 kV bus #1 exposing it to faults and scheduled maintenance outages 345/138 kV Transformer #11B Transformer 11B was manufactured in 1997 with increased tertiary bushing power factor indicating capacitive layer deterioration. The change in bushing dielectric data indicates the tertiary bushings are at greater risk of failure or loss of service of the transformer. Also, observed elevated levels of carbon monoxide and carbon dioxide indicates decomposition of the paper insulation that impairs the units ability to withstand future short circuit or through fault events Unit leaks oil Connected in parallel with transformer 11A; high-side connected directly to 345 kV bus #1 exposing it to faults and scheduled maintenance outages 345/138 kV Transformer #3 High-side connected to 345 kV bus #2 via Motor Operated Air-Break Switch (MOAB) exposing the bus to momentary transformer fault events 31 of the 94 microprocessor relays in the Cloverdale 138 kV Station utilize obsolete firmware 69 kV hook-stick circuit breaker and switcher disconnect switches identified in need of replacement with Gang Operated Air-Breaker Switches (GOAB)
AEP-2020-OH013 | AEP | PJM West | 2020-02-21 | 2020-06-19 | 2020-09-15 | s2284 |  | Columbus, OH | Canal Street – Marion Road 138 kV Underground Circuit • Ohio Department of Transportation (ODOT) has requested that approximately 1500 feet of the existing Canal – Marion 138 kV underground circuit be relocated as part of a planned Interstate improvement project. • The existing Canal – Marion 138 kV underground circuit is approximately 3.8 miles long and was originally installed in the 1950’s. • The circuit utilizes an underground oil-filled pipe type cable design. Oil-filled pipe type underground cables come with several challenges/risks in densely populated urban areas. Lead times for replacement/repairs from the remaining single vendor can be 6 months to a year. Even minor issues with the cable could result in costly outages over an extended period of time due to this single remaining vendor
AEP-2020-OH014 | AEP | PJM West | 2020-02-21 | 2020-03-19 | 2020-05-11 | S2224 |  | Athens Area Improvement | Poston – Shrouds Run 138kV (1965) • Length 7.52 Miles • Original Construction Type: Wood H-Frame • Original Conductor Type: 636 ACSR Conductor (vintage 1966) • Momentary/Permanent Outages: 3 total outages last 5 years • Number of open conditions: 62 • Total structure count: 46 • Open conditions include: rot top, woodpecker holes, bowed structures, and burnt poles • Unique structure count with open conditions: 31
AEP-2020-OH015 | AEP | PJM West | 2020-04-20 | 2020-09-11 | 2021-01-13 | s2394.1-.7 |  | Haviland, Ohio | Haviland – South Hicksville 69kV Original Install Date: 1927 • Length of Line: 26.15 • Total structure count: 560 • Original Line Construction Type: Wood • 16% of structures recently replaced (~2.5 miles) • Wooden Cross Arms • Horizontal Ceramic insulators • Conductor Type: 336.4 KCM ACSR 18/1 Merlin (original 1927 install)CONDITION / PERFORMANCE / RISK ASSESSMENT: • Outage History • Momentary/Permanent Outages and Duration: 12 Momentary and 8 Permanent – average duration of 26.32 hours • CMI: 8.2 M • No automatic line sectionalizing scheme through the entire length of this line. • Condition Summary • Number of open conditions by type / defects / inspection failures: 40 open conditions on 39 unique structures • Open conditions / defects / inspection failures include: broken structures, rotting structures, burnt conductors, broken/missing ground lead Risk • Number of Customers at Risk: 9,639 • Load at Risk: 17.794 MVA • The Antwerp (Paulding Putnam Co-op) customer is served off of a hard tap.
APS-2020-007 | APS | PJM West | 2020-05-22 |  |  |  |  | Butler - Karns City - Kissinger Junction 138 kV Line | Loss of the Karns City #1 or #2 138-25 kV transformer results in significant voltage drop on the 25 kV system. Karns City substation consists of: Two distribution transformers connected to transmission with switches Two networked 138 kV transmission lines Transmission lines are limited by terminal equipment. Karns City – Butler 138 kV existing line rating is 141 / 179 MVA (SN/SE). The existing transmission line conductor rating is 160 /192 MVA (SN/SE). (substation conductor) Refer to APS-2019-015. Karns City – Kissinger Junction 138 kV existing line rating is the existing transmission line conductor rating of 221 / 268 MVA (SN/SE). The winter emergency line rating is limited to 306 MVA from 317 MVA. (line relaying) Refer to APS-2020-009.
AEP-2020-OH017 | AEP | PJM West | 2020-03-19 | 2020-12-18 |  |  |  | Hemlock – Bryson 69kV | Buckeye Rural Electric Cooperative, Inc. has requested 69kV service to a new delivery point near AEP’s Hemlock station by December 2022. Anticipated load is approximately 2.6 MW of transferred load.
APS-2020-009 | APS | PJM West | 2020-05-22 |  |  |  |  | Karns City – Kissinger Junction 138 kV Line ¦ Armstrong – Kissinger Junction 138 kV Line ¦ Burma – Kissinger Junction 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2020-009 ¦ Karns City – Kissinger Junction 138 kV Line¦221 / 268 ¦ 221 / 268 ¦Line Relaying (existing rating 306 MVA (WE) conductor rating 317 MVA (WE) ¦Armstrong – Kissinger Junction 138 kV Line¦221 / 268 ¦ 221 / 268 ¦ N/A ¦ Burma – Kissinger Junction 138 kV Line¦ 293 / 332 ¦ 308 / 376 ¦ Substation Conductor, Line Relaying, Line Trap, Circuit Breaker¦
AEP-2020-OH021 | AEP | PJM West | 2020-04-20 | 2020-12-18 |  |  |  | Putnam/Hancock County | Line Name: Kalida – Rockhill 34.5 kV Original Install Date (Age): 1923 Length of Line: 17.22 miles Total structure count: 451 Original Line Construction Type: Wood Monopoles 96% of structures are from 1923, remaining 4% from 2000’s. Short wood poles susceptible to vegetation outages outside of the ROW. Wooden Crossarm construction with vertical post insulators. Conductor Type: #1 Copper from 1923 (99%), remaining 795 ACSR (<1%) 5 Year Outage History Momentary/Permanent Outages: 2 Momentary CMI: 222,797 Condition Summary Number of open conditions: 6 Additional Information The line is insulated with vertical post insulators which do not meet current AEP standards for CIFO and minimum leakage distance requirements. The line shielding angle on the typical tangent structure is measured at 45 °, which is inadequate for AEP current shielding angle requirements. The wood structure’s current age is 191% of the 95% Probability of Failure (POF) of 51 years. The shield wire's current age is 134% of the 95% POF of 72 years. The insulator's current age is 111% of the 95% POF of 87 years. The POF values are based on CEATI Report No T144700-3257 Customer Service: AEP Ohio has requested new service to replace their existing Jones City Station, which has conditions on the AEP Ohio assets (Transformer is 70 years old with existing conditions).
AEP-2020-OH025 | AEP | PJM West | 2020-04-20 | 2020-06-19 | 2020-09-15 | s2284 |  | Columbus, OH | Canal Street 138kV 138 kV Circuit Breaker (4): • Install Date: 1969 • Interrupting Medium: Oil • Additional Information: – Interrupting Capability: 37kA – Fault Operations: • Number of Fault Operations: 15 • Manufacturer recommended Number of Operations: 10 – Oil breaker maintenance has become more difficult due to the oil handling required to maintain them. Oil spills are frequent with breaker failures and routine maintenance and can become an environmental hazard. This is the last remaining oil breaker at Canal Street station.
AEP-2020-OH027 | AEP | PJM West | 2020-04-20 | 2020-09-11 | 2021-01-13 | s2396 |  | Walnut Creek Capacitor Bank | Holmes-Wayne Electric Cooperative has an urgent large block load increase and is replacing their Trail substation transformer with a larger unit. The anticipated new load is 8 MW. The load will be added incrementally starting in August 2020.
AEP-2020-OH030 | AEP | PJM West | 2020-05-22 | 2020-10-16 |  |  |  | Wood County, Ohio | Hancock-Wood Co-op has requested a new service to replace their existing Hatton Delivery Point. Hatton delivery point is currently served via a hard tap from the Pemberville (FE) – West End Fostoria (AEP) 69kV circuit. The new customer station is being built to adjacent to their existing substation. The hard tap limits operational capabilities for this circuit. It is difficult to coordinate maintenance efforts because any work on the section from Longley Switch to Pemberville (FE) involves outage to the Hatton Delivery Point. Load is approximately 2.26 MVA CMI: There were no unplanned outages, but there were six scheduled and one monetary outages that affected the customer, in the last 5 years.
AEP-2020-OH031 | AEP | PJM West | 2020-05-22 | 2020-10-16 |  |  |  | Wood County, Ohio | Paulding – Putnam Electric Co-op is replacing their 3.75 MVA transformer with a 12/16/20 MVA transformer, which requires some changes to their delivery point. This delivery point is served by the North Cecil switch on the Mark Center – Paulding 69 kV circuit. North Cecil has no auto-sectionalizing capability. Load: The Co-op delivery point serves approximately 4.9 MW CMI: In the last 5 years, there were 6 unscheduled outages affecting the customer, 3 of which were momentary and 3 were permanent outages. The 5-year CMI experienced by this customer is 170,520.
AEP-2020-OH035 | AEP | PJM West | 2020-07-17 | 2020-11-20 |  |  |  | Lima Ohio | A request has been made by a customer to provide service for a 1.7 MW load to be connected to the Shawnee Road – Sterling 34.5kV circuit.
AEP-2020-OH036 | AEP | PJM West | 2020-08-14 | 2020-10-16 |  |  |  | Reedurban Transformer | Station Name: Reedurban The 138-69kV transformer has failed and has been temporarily replaced with a mobile 138-69kV transformer. Manufactured and installed in 1988. 60 MVA nameplate, Westinghouse unit. Failure attributed to significant deterioration of transformer windings
AEP-2020-OH040 | AEP | PJM West | 2020-09-11 | 2021-02-17 |  |  |  | Payne 69kV | Station Payne 69kV Two (2) 69 kV circuit breakers are oil filled breakers of 1960s vintage without oil containment and have exceeded the recommended fault operations of 10. These breakers have 66 and 46 fault operations respectively. Additionally, oil filled breakers require frequent maintenance. Oil spills are common and can result in significant environmental mitigation costs. 21 out 23 relays are electromechanical and 2 are static relays without vendor support, fault data collection, or SCADA ability. The 69/12 kV transformer is a fused bank with no disconnecting/sectionalizing capability. Low side breakers need to be opened to be able to safely work on the fuse and/or transformer.
AEP-2020-OH043 | AEP | PJM West | 2020-10-16 | 2020-12-18 |  |  |  | Ross County, Ohio | The condition of Slate Mills is very unsafe; the structures have been deemed a failure the week of August 17th 2020. Much of the wooden structures are in a state where collapse could easily happen. Any attempt at repair would be dangerous and might precipitate the collapse that we would be trying to mitigate.
AEP-2020-OH047 | AEP | PJM West | 2020-11-20 | 2021-02-17 |  |  |  | North Strasburg, Ohio | Station North Strasburg 138kV CONDITION / PERFORMANCE / RISK ASSESSMENT: Equipment Concerns: • The station utilizes two circuit switchers for 138kV sectionalizing devices on the through-path. The circuit switchers have failed and are no longer operable. They have been disabled to avoid a system misoperation. • 1966 vintage, S&C Electric type ‘G’ model (both switchers) • The motor mechanisms and relays no longer function properly. Other Station Concerns: • The circuit switchers are installed on deteriorating wood structures.
APS-2019-009 | APS | PJM West | 2019-06-28 | 2019-12-18 | 2020-02-19 | s2045.2 |  | Armstrong – New Bethlehem 138 kV Line, New Bethlehem – Brookville 138 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦PN-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦----------¦------------------------------------------¦--------------------------------¦-------------------------------------¦-----------------------------¦ ¦ 025 / APS-2019-009 ¦ Armstrong – New Bethlehem 138 kV Line, New Bethlehem – Brookville 138 kV Line ¦ 293/332, 295/342 ¦ 308/376 ,308/376 ¦ Line Trap, Substation Conductor, Line Trap, Substation Conductor, Circuit Breaker ¦
APS-2019-010 | APS | PJM West | 2019-07-11 | 2019-08-08 | 2020-02-19 | s2052.1 |  | Elko – Shawville 230 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Elko – Shawville 230 kV Line Exiting line rating: 489/554
APS-2019-011 | APS | PJM West | 2019-07-11 | 2019-08-08 | 2020-02-19 | s2051.2 |  |  | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Shawville – Shingletown 230 kV Line Exiting line rating: 489/554
APS-2019-012 | APS | PJM West | 2020-04-20 | 2020-05-22 | 2020-10-05 | s2288 |  |  | New Customer Connection – A customer requested 138 kV service, anticipated load is 27 MW, location is near the Buckhannon – Corder Crossing (Pruntytown) 138 kV line.
ATSI-2019-059 | ATSI | PJM West | 2019-07-24 |  |  |  |  | McDowell - Sharon (Y-300) 69 kV Line (18.8 Miles) | Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life Transmission line ratings are limited by terminal equipment. ¦ Locale ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Circuit MVA Rating (SN / SE) ¦ Existing Conductor MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ Length of Line (miles) ¦ Identified Structures (end of life / total) ¦ Failure reasons ¦ ¦--------¦------------¦------------------------------------------¦---------------------------------------¦-----------------------------------------¦-----------------------------¦------------------------¦---------------------------------------------¦-----------------¦ ¦ McDowell - Sharon (Y-300) 69 kV Line (18.8 Miles) ¦ -059 ¦ McDowell - Dept. of Corrections ¦ 47 / 48 ¦ 47 / 56 ¦ Relay ¦ 6.0 ¦ 195 / 235 (83% Failure Rate) ¦ Woodpecker holes, decay and age ¦ ¦-¦-¦ Dept. of Corrections - Mercer Forge ¦ 47 / 56 ¦ 47 / 56 ¦ - ¦ 1.0 ¦-¦-¦ ¦-¦-¦ Mercer Forge - Reznor Tap ¦ 47 / 56 ¦ 47 / 56 ¦ - ¦ 0.3 ¦-¦-¦ ¦-¦-¦ Reznor Tap - Mercer Tap ¦ 47 / 56 ¦ 47 / 56 ¦ - ¦ 1.1 ¦-¦-¦ ¦-¦-¦ Mercer Tap - Sharon 69kV ¦ 72 / 72 ¦ 80 / 96 ¦ Relay ¦ 10.4 ¦-¦-¦
ATSI-2019-060 | ATSI | PJM West | 2019-07-24 |  |  |  |  | East Springfield - London 69 kV Line (29.7 Miles) | Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life Transmission line ratings are limited by terminal equipment. ¦ Locale ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Circuit MVA Rating (SN / SE) ¦ Existing Conductor MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ Length of Line (miles) ¦ Identified Structures (end of life / total) ¦ Failure reasons ¦ ¦--------¦------------¦------------------------------------------¦---------------------------------------¦-----------------------------------------¦-----------------------------¦------------------------¦---------------------------------------------¦-----------------¦ ¦ East Springfield - London 69 kV Line (29.7 Miles) ¦ -060 ¦ East Springfield - Titus Tap ¦ 45 / 48 ¦ 45 / 54 ¦ Relay ¦ 4.7 ¦ 273 / 449 (61% Failure Rate) ¦ Decay/rot and age ¦ ¦-¦-¦ Titus Tap - Plattsburg Tap ¦ 45 / 54 ¦ 45 / 54 ¦ - ¦ 5.6 ¦-¦-¦ ¦-¦-¦ Plattsburg Tap - London Cor. Tap ¦ 45 / 54 ¦ 45 / 54 ¦ - ¦ 7.5 ¦-¦-¦ ¦-¦-¦ London Cor. Tap - Big Plain Tap ¦ 76 / 92 ¦ 76 / 92 ¦ - ¦ 11.1 ¦-¦-¦ ¦-¦-¦ Big Plain Tap - London 69kV Line ¦ 76 / 92 ¦ 76 / 92 ¦ - ¦ 0.8 ¦-¦-¦
APS-2019-014 | APS | PJM West | 2019-12-18 | 2020-03-19 | 2020-05-15 | s2205 |  | Pittsburgh Mills – Springdale 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2019-014 ¦ Pittsburgh Mills – Springdale 138 kV Line ¦ 293/302 ¦ 296/332 ¦ Line Trap ¦
APS-2020-002 | APS | PJM West | 2020-04-21 | 2020-07-17 | 2020-10-05 | S2289 |  | Roxbury – Greene 138 kV Line ¦ Greene – Letterkenny 138 kV Line ¦ Letterkenny – Grand Point 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2020-002 ¦ Roxbury – Greene 138 kV Line¦ 164 / 206 ¦ 221 / 268 ¦ Disconnect Switch, Substation Conductor¦ Greene – Letterkenny 138 kV Line¦ 221 / 268 ¦ 221 / 268 ¦ N/A ¦ Letterkenny – Grand Point 138 kV Line¦ 196 / 228 ¦ 221 / 268 ¦Line Trap ¦
APS-2020-004 | APS | PJM West | 2020-05-22 | 2020-07-17 | 2020-10-05 | S2290 |  | Cabot – Lawson Junction 138 kV Line ¦ McCalmont – Lawson Junction 138 kV Line ¦ Fawn – Lawson Junction 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2020-004 ¦ Cabot – Lawson Junction 138 kV Line¦ 287 / 287 ¦ 297 / 365 ¦ Line Relaying, Line Trap ¦ McCalmont – Lawson Junction 138 kV Line¦ 287 / 287 ¦ 297 / 365 ¦ Substation Conductor, Line Relaying, Line Trap¦ ¦ Fawn – Lawson Junction 138 kV Line¦ 294 / 342 ¦ 308 / 376 ¦ Substation Conductor, Line Trap¦
APS-2020-005 | APS | PJM West | 2020-05-22 | 2020-07-17 | 2020-10-05 | S2291 |  | Charleroi – Union Junction 138 kV Line ¦ Mitchell – Union Junction 138 kV Line ¦ Peters – Union Junction 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2020-005 ¦ Charleroi – Union Junction 138 kV Line¦ 274 / 302 ¦ 296 / 302 ¦ Substation Conductor, Line Trap ¦Mitchell – Union Junction 138 kV Line¦ 295 / 342 ¦ 308 / 376 ¦ Substation Conductor, Line Trap¦ ¦Peters – Union Junction 138 kV Line¦ 294 / 342 ¦ 308 / 376 ¦ Substation Conductor, Line Trap¦
APS-2020-006 | APS | PJM West | 2020-05-22 | 2020-07-17 | 2020-10-05 | S2292 |  | Gordon – Lagonda 138 kV Line ¦ Lagona – Windsor 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2020-006 ¦ Gordon – Lagonda 138 kV Line¦ 293 / 343 ¦ 309 / 376 ¦ Substation Conductor, Line Relaying, Line Trap ¦Lagona – Windsor 138 kV Line ¦ 261 / 311 ¦ 308 / 376 ¦ Substation Conductor, Line Relaying, Line Trap
APS-2020-008 | APS | PJM West | 2020-05-22 | 2020-07-17 | 2020-10-05 | S2314.2 |  | Blairsville East – Social Hall 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need # ¦Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ APS-2020-008 ¦ Blairsville East – Social Hall 138 kV Line¦225 / 287¦ 243 / 294 ¦ Substation Conductor, CTs, Line Relaying, Line Trap¦
APS-2020-010 | APS | PJM West | 2020-05-22 | 2020-07-17 | 2020-10-05 | S2293 |  | Rider - Weston 138 kV Line | New Customer Connection – A customer requested 138 kV service, anticipated load is 10 MW, location is near the Rider – Weston 138 kV line.
APS-2020-011 | APS | PJM West | 2020-05-22 | 2020-10-06 | 2020-11-11 | S2386 |  | Doubs - Goose Creek 500 kV | Doubs – Goose Creek 500 kV line is exhibiting deterioration. The transmission line was constructed in 1966. Total line distance is approximately 18 miles (FirstEnergy owns 15 miles). FirstEnergy owns 77 structures of the transmission line which consists of 69 COR-TEN steel lattice structures and eight galvanized steel structures. Independent assessment was conducted on a sample of 11 structures. 10 of the 11 structures failed inspection (90% failure rate). Failure reasons include packout, corrosion, tension cracking, and structure foundation cracks/deterioration. Transmission line ratings are limited by external ratings and terminal equipment
ATSI-2018-009 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2020-03-18 | s1987 |  |  | Avon-Fowles 138 kV Q1 and Q3 Line Load at Risk * Reduce the amount of local load loss at risk and mitigate non-planning criteria voltage concerns on the > 100 kV system under contingency conditions. - Loss of Avon-Fowles Q1 138kV line (“B_LINE1_NR_006”) and path-end outage of the Avon-Fowles Q3 138 line. - Results in the potential loss of approximately 60 MWs and 14,000 customers. - Results in the potential low voltage (0.91 p.u.) at Dawson 138kV Substation Or - Common tower outage Avon-Fowles Q1 138kV line and the Avon-Fowles Q3 138 line (“C5-TWL-NR005”). - Results in the consequential load loss of approximately 237 MWs and 68,200 customers.
ATSI-2019-070 | ATSI | PJM West | 2019-07-24 |  |  |  |  | Walmo 69 kV Area Need | Walmo 69 kV Area * The Cedar Street-Grant Street 69 kV line serves roughly 18.6 MW and 5,287 customers on a 5.8 mile radial with a normally open point near Walmo substation. * The Cedar Street-Grant Street 69 kV Line has experienced 5 outages in the past 5 years (3 sustained) * After the construction of the Shenango 69 kV switching station (s1712 / ISD 12/31/2021) the newly networked Cedar Street-Shenango #2 69 kV line (formally the Cedar Street-Cascade 69 kV and Cedar Street-New Wilmington 69 kV lines) will serve approximately 44.2 MW and 10,842 customers with total line exposure of 23 miles. Walmo substation is currently served from this transmission line. * The Cedar Street-Shenango #2 69 kV Line is exhibiting an upward trend in both minor and major maintenance, with several recent ground-line rejects. * 58% Rejection Rate (191 / 327) * Overall condition, age, woodpecker holes, broken grounds and insulator bells. * 9 line switches on the circuit are aged and do not meet current established design standards * Experienced 8 outages in the past 5 years (all sustained)
ATSI-2018-021 | ATSI | PJM West | 2018-11-29 | 2019-02-20 | 2020-03-18 | s1872 |  | Medina-Medina Industries 69 kV | New Customer Connection - A customer requested 69 kV service for load of approximately 10 MVA near the Medina-Medina industries 69 kV line.
ATSI-2018-023 | ATSI | PJM West | 2018-11-29 | 2019-02-20 |  | s1873 |  | Black River 138 kV | Black River 138 kV Area * Thermal constraints identified in previous Gen Queue and Gen Deliverability Studies. * Future year analysis shows potential thermal constraints. ―For the loss of the Avon-Beaver #1 345 kV Line and the Avon-Beaver #2 345 kV Line results in the Charleston-Lorain 138 kV Line loading to greater than 90%.
ATSI-2019-009 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  | s1953 |  | Maroe-Malinta 34.5 kV Area | Maroe-Malinta 34.5 kV Area * The existing Richland-Maroe 34.5kV line is a radial line with limited capability of transferring load onto different circuits for emergency restoration and scheduling of routine maintenance. * The loss of the Richland-Maroe 34.5 kV radial line results in the loss of approximately 8 MW and 2,550 customers at two (2) sub-transmission service points. * The existing Weston-Malinta 34.5 kV line is a radial line with limited capability of transferring load onto a different circuits for emergency restoration and scheduling of routine maintenance. * The loss of the Weston-Malinta 34.5 kV radial line results in the of approximately 6 MW and 1,000 customers at two (2) sub-transmission service points. * The 138 / 34.5 kV transformer #1 at Richland substation is greater than 70 years old and is showing signs of end of life; including oil leaks, failing components, and increasing maintenance. * The 69 / 34.5 kV transformer #3 at Westin substation is greater than 74 years old and is showing signs of end of life; including oil leaks and deteriorating components. * Customers taking sub-transmission service on these two radial lines have requested additional reliability and operational flexibility. - The 34.5kV radial lines cannot be networked due to insufficient short circuit current. - The Westin 69 / 34.5 kV transformer #3 (end of life) does not have the capacity to carry the entire load on a networked 34.5 kV system for a path end outage at Richland substation.
ATSI-2019-010 | ATSI | PJM West | 2019-01-11 | 2019-11-22 |  |  |  | Valley Substation | Valley & Thiess 138 kV Substation Area The Valley and Thiess 138 kV substations are presently owned by Cuyahoga Falls Municipality with transmission service from the ATSI Babb-Chamberlin 138 kV line. * A transmission line outage of the double circuit networked 138 kV tap (approximately 1 mile) to Valley substation could result in approximately 86 MW and 25,000 Customers interrupted for an extended period of time. * The loss of the Chamberlin-Thiess 138 kV line, followed by the loss of the Babb-Valley 138 kV line (N-1-1) could result in approximately 106 MW and 25,000 customers interrupted for an extended period of time. Evans & Darrow 138 kV Substation Area * The loss of the Babb-Evans 138 kV line, followed by the loss of the East Akron-Evans 138 kV line (N-1-1) results in approximately 25 MW and 4,834 customers interrupted. * The loss of the Chamberlin-Hudson Muni 138 kV line, followed by the loss of the Brady-Hanna 138 kV line (N-1-1), results in approximately 61 MW and 18,800 customers interrupted. Post-contingency voltage drops below 0.92 p.u. in the Darrow substation area. * Over the past five years, - The Chamberlin-Theiss 138 kV line has experienced five (5) outages (3 sustained, 2 momentary) - The Theiss-Valley 138 kV line has experienced one (1) outage (1 sustained, 0 momentary) - The Chamberlin-Hudson Muni 138 kV line has experienced four (4) outages (2 sustained, 2 momentary) - The Babb-Evans 138 kV line has experienced one (1) outage (1 sustained, 0 momentary)
ATSI-2019-015 | ATSI | PJM West | 2019-01-11 | 2019-03-25 | 2020-07-02 | S2259 |  | Ashtabula 138 kV | Ashtabula 138 kV Substation Equipment and Protection * Two (2) 138 kV breakers (B143 & B149), lightning arresters and associated switches, and control wiring are showing degrading performance, increasing maintenance, age (46-63 years), and obsolescence of equipment and spare parts
ATSI-2019-016 | ATSI | PJM West | 2019-01-11 | 2020-04-20 | 2020-07-02 | s2245 |  | Chamberlin 138 kV | Chamberlin 138 kV Substation * Two (2) 138 kV Oil Circuit Breaker (OCB) breakers (B86 & B69) and MOAB Switch A19 at Chamberlin are showing degrading performance, increasing maintenance, age (> 30 years), and obsolescence of equipment and spare parts.
ATSI-2019-050 | ATSI | PJM West | 2019-02-07 | 2019-03-07 | 2020-07-02 | S2260 |  | Ashtabula 345 kV | Perry-Ashtabula-Erie West 345 kV Line and Surrounding Areas * Perry-Ashtabula-Erie West 345 kV Line is a three terminal line. * Three terminal lines are prone to mis-operations, lengthy fault locating analysis and longer restoration efforts. * Existing transmission relay communication equipment is approaching end of life, is obsolete, and is difficult to maintain and repair. * Non-planning criteria violation voltage concerns on the > 100 kV system under contingency conditions. - Loss of the Perry-Ashtabula-Erie West 345 kV (or the Ashtabula 345/138kV TR) followed by the loss of Leroy Center-Stacy Q3 138 kV line. OR - Loss of Leroy Center-Ashtabula Q4 138 kV line followed by the loss of the Leroy Center-Stacy Q3 138 kV line. Results in low voltage and potential local voltage collapse at Stacy substation; load shed of approximately 75 MWs is necessary to maintain system voltages.
ATSI-2019-051 | ATSI | PJM West | 2019-02-20 | 2019-04-23 | 2020-03-18 | s2067 |  | Pine-Warrendale 69 kV | Pine-Warrendale 69 kV Condition Assessment * Warrendale-Richard segment of the line (approximately 3.6 miles of the 6.42 mile line) has been identified as having obsolete and deteriorated equipment. - Damaged conductor identified along the line. - Construction is mostly 42 year old construction; poor inspection results. * Customers and load at risk: 6,135 customers and 22 MWs of load. * The Pine-Warrendale 69 kV line has experienced 4 outages in the past five years.
ATSI-2019-054 | ATSI | PJM West | 2019-03-25 | 2019-05-20 | 2020-03-18 | s2068 |  | Ottawa-West Fremont No.2 138 kV line | Ottawa-West Fremont #2 138 kV Equipment and Tap Connection * The existing KPF switches A-13135 and A-13136 are obsolete and no longer supported by the manufacturer. The existing customer tap connection (tapped between switch A-13135 and switch A-13136) on the Ottawa-West Fremont #2 138 kV line requires a 270 degree turn and crosses under both the Ottawa-West Fremont #1 and Ottawa-West Fremont #2 138 kV lines which creates operational maintenance constraints.
ATSI-2019-057 | ATSI | PJM West | 2019-05-20 | 2019-07-24 | 2020-03-18 | s2064 |  | Ashtabula | New Customer Connection - A customer requested 138 kV transmission service approximately 75 MVA of load be connected to the Ashtabula 138 kV substation, approximately 1.7 miles from the customer substation.
ATSI-2019-058 | ATSI | PJM West | 2019-07-24 | 2019-11-22 | 2020-03-18 | s2121 |  | Lemoyne | A customer requested a 138 kV transmission service for a 138/12.47 kV substation with approximately 10.0 MVA of load near Lemoyne substation.
ATSI-2019-061 | ATSI | PJM West | 2019-07-24 | 2019-11-22 | 2020-03-18 | s2122 |  | Darrow - Shalersville 69 kV Line (11.2 Miles) | Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life Transmission line ratings are limited by terminal equipment. ¦ Locale ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Circuit MVA Rating (SN / SE) ¦ Existing Conductor MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ Length of Line (miles) ¦ Identified Structures (end of life / total) ¦ Failure reasons ¦ ¦--------¦------------¦------------------------------------------¦---------------------------------------¦-----------------------------------------¦-----------------------------¦------------------------¦---------------------------------------------¦-----------------¦ ¦ Darrow - Shalersville 69 kV Line (11.2 Miles) ¦ -061 ¦ Darrow - Little Tikes Tap ¦ 76 / 92 ¦ 76 / 92 ¦ - ¦ 0.7 ¦ 59 / 178 (33% Failure Rate) ¦ Decay, woodpecker holes, and age ¦ ¦-¦-¦ Little Tikes Tap - Streetsboro ¦ 76 / 92 ¦ 76 / 92 ¦ - ¦ 4.3 ¦-¦-¦ ¦-¦-¦ Streetsboro - Streetsboro ¦ 76 / 92 ¦ 76 / 92 ¦ - ¦ 1.8 ¦-¦-¦ ¦-¦-¦ Streetsboro - Aurora Plastics Tap ¦ 82 / 103 ¦ 100 / 121 ¦ Switch ¦ 2.2 ¦-¦-¦ ¦-¦-¦ Aurora Plastics Tap - Shalersville ¦ 100 / 104 ¦ 100 / 121 ¦ Relay ¦ 2.2 ¦-¦-¦
ATSI-2019-062 | ATSI | PJM West | 2019-07-24 | 2019-11-22 | 2020-03-18 | s2123 |  | Clark - Navistar 69 kV Line (11.3 Miles) | Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life Transmission line ratings are limited by terminal equipment. ¦ Locale ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Circuit MVA Rating (SN / SE) ¦ Existing Conductor MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ Length of Line (miles) ¦ Identified Structures (end of life / total) ¦ Failure reasons ¦ ¦--------¦------------¦------------------------------------------¦---------------------------------------¦-----------------------------------------¦-----------------------------¦------------------------¦---------------------------------------------¦-----------------¦ ¦ Clark - Navistar 69 kV Line (11.3 Miles) ¦ -062 ¦ Clark - Ferncliff 69kV Line ¦ 76 / 92 ¦ 76 / 92 ¦ - ¦ 2.9 ¦ 93 / 185 (50% Failure Rate) ¦ Age, woodpecker holes, grounding not present ¦ ¦-¦-¦ Ferncliff - Ridgewood 69 kV Line ¦ 76 / 92 ¦ 76 / 92 ¦ - ¦ 1.0 ¦-¦-¦ ¦-¦-¦ Ridgewood - Navistar 69 kV Line ¦ 45 / 54 ¦ 45 / 54 ¦ - ¦ 7.4 ¦-¦-¦
ATSI-2019-063 | ATSI | PJM West | 2019-07-24 | 2019-11-22 | 2020-03-18 | s2124 |  | Avery Substation No.1 Transformer 138/69 kV | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -063 ¦ Avery Substation No.1 Transformer 138/69 kV ¦ 153 / 153 ¦ 177 / 209 ¦ Line Relay, Substation Conductor ¦
ATSI-2019-064 | ATSI | PJM West | 2019-07-24 | 2019-11-22 | 2020-03-18 | s2125 |  | Cloverdale - Canton Central 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -064 ¦ Cloverdale - Canton Central 138 kV Line ¦ 161 / 194 (S), 182 / 210 (W) ¦ 161 / 194 (S), 182 / 230 (W) ¦ Line Relay (Winter Ratings) ¦
ATSI-2019-065 | ATSI | PJM West | 2019-07-24 | 2019-11-22 | 2020-03-18 | s2126 |  | Evergreen - Ivanhoe 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -065 ¦ Evergreen - Ivanhoe 138kV Line ¦ 200 / 242 (S), 226 / 249 (W) ¦ 200 / 242 (S), 226 / 286 (W) ¦ Line Relay (Winter Rating) ¦
ATSI-2019-066 | ATSI | PJM West | 2019-07-24 | 2019-11-22 | 2020-03-18 | s2127 |  | Hoytdale - New Castle No.2 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -066 ¦ Hoytdale - New Castle No.2 138 kV Line ¦ 329 / 373 ¦ 425 / 522 ¦ Relay, Substation Conductor, Disconnect Switch ¦
ATSI-2019-089 | ATSI | PJM West | 2019-11-22 |  |  |  |  | Brush Wellman-Genoa 69kV Line - Need | Brush Wellman-Genoa 69kV The existing 69 kV transmission line is approximately 11.4 miles long with approximately 20 MWs of load and 2,592 customers at risk. It has four transmission service connection points. 83% of the wood poles failed recent line inspection. Typical age of the line components is 59 years. Six (6) obsolete line switches System performance over the past five years: 1 momentary / 0 sustained
ATSI-2019-067 | ATSI | PJM West | 2019-07-24 | 2019-11-22 | 2020-03-18 | s2128 |  | Crossland - Shenango No.2 138 kV | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ ATSI-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -067 ¦ Crossland - Shenango No.2 138 kV ¦ 215 / 215 ¦ 278 / 339 ¦ Relay, Substation Conductor ¦
ATSI-2019-068 | ATSI | PJM West | 2019-07-24 | 2020-05-22 | 2020-10-01 | S2262 |  | Salt Spring 138 kV Substation Need | Salt Springs 138 kV Substation * System analysis shows that after a Salt Springs 138 kV Bus Fault (ATSI-P2-2-OEE138-019) a substantial amount of load is at risk (Approximately 138 MW). * Bus blocking scheme in place is complicated and requires multiple relays to all function properly for every internal and external fault. * The 138 kV breakers B35, B56, B40, B2, B42, B45 do not have enough CTs for separate inputs to a primary and backup differential scheme. * Relays on the Salt Springs-Riverbend 138 kV Line and the relays on the Salt SpringsMasury 138 kV Line have a history of misoperation. * Breakers B35 and B45 are oil circuit breakers over 45 years old
ATSI-2019-069 | ATSI | PJM West | 2019-07-24 | 2020-05-22 | 2020-10-01 | S2263 |  | Sharon Substation 138 kV Need | Sharon 138 kV Substation * Increasing maintenance costs for 138 kV breakers B-48 and B-60 * Breakers B-48 and B-60 are over 30 years old * CCVT's are over 25 years old
ATSI-2019-072 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2227 |  | Relay Misoperation | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -72 ¦ Eber-Swanton 138 kV Line ¦ 327 / 396 ¦ 327 / 420 ¦ Substation Conductor (Winter Ratings) @ Swanton ¦
ATSI-2019-073 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2228 |  | Eastlake-Lloyd 138 kV Q12 Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -73 ¦ Eastlake-Lloyd 138 kV Q12 Line ¦ 103 / 132 ¦ 148 / 151 ¦ Substation Conductor, Relay, CTs @ Lloyd ¦
ATSI-2019-074 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2229 |  | Chamberlin-Hudson East 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦¦ -74 ¦ Chamberlin-Hudson East 138 kV Line ¦ 226 / 249 ¦ 226 / 286 ¦ Relay (Winter Ratings) @ Chamberlin ¦
ATSI-2019-075 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2230 |  | Eastlake-Nottingham 138 kV Q11 Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -75 ¦ Eastlake-Nottingham 138 kV Q11 Line ¦ 324 / 382 ¦ 324 / 395 ¦ Meter, Relay @ Eastlake ¦
ATSI-2019-076 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2231 |  | Maclean-Lemoyne 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -76 ¦ Maclean-Lemoyne 138 kV Line ¦ 329 / 413 ¦ 376 / 465 ¦ Disconnect Switch @ Maclean ¦
ATSI-2019-077 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2232 |  | Clinton-CPP 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -77 ¦ Clinton-CPP 138 kV Line ¦ 187 / 222 ¦ 194 / 237 ¦ Substation Conductor @ Clinton ¦
ATSI-2019-078 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2233 |  | Eastlake-Jordon 138 kV Q14 Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -78 ¦ Eastlake-Jordon 138 kV Q14 Line ¦ 261 / 317 ¦ 273 / 332 ¦ Substation Conductor, Meter, Relay @ Eastlake & Jordon ¦
ATSI-2019-079 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2234 |  | Beaver-West Lorain 345 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -79 ¦ Beaver-West Lorain 345 kV Line ¦ 1370 / 1720 ¦ 1560 / 1900 ¦ Substation Conductor, Disconnect Switch @ Beaver ¦
ATSI-2020-012 | ATSI | PJM West | 2020-06-19 |  |  |  |  | Ford Rd | Ford Road-Maclean and Gould-Maclean 69 kV Line  For a N-1-1 contingency, a Ford Road-Maclean 69 kV line fault and the Gould-Maclean 69 kV Line fault, local load loss of 61 MW is observed affecting over 5,600 customers.  The Ford Road-Maclean 69 kV line has approximately 5.8 miles of line exposure. Additionally Pilkington tap adds another 2.3 miles of line exposure to the Ford Road-Maclean 69 kV line. This line servers approximately 38 MW and over 3,800 customers. This line has experienced three sustained outages in the last five years (2015-2019) with an average duration of 6.5 hours.  The Gould-Maclean 69 kV line has approximately 7.9 miles of line exposure. Additionally, the Pilkington tap and Penta County tap adds another 3.1 miles of line exposure to the Gould-Maclean 69 kV line. This line servers approximately 23 MW and over 1,800 customers. This line has experienced one sustained outage in the last five years (2015-2019) with a duration of 18.6 hours.
ATSI-2019-080 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2234 |  | Bluebell 138 kV Bus Protection | FirstEnergy has identified protection schemes on networked lines and buses using a certain vintage of relays that have a history of misoperation. Schemes protecting these facilities have no local backup so failures impact a larger portion of the system. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ - 080 ¦ Bluebell 138 kV Bus Protection ¦ 100 / 100 ¦ 164 / 206 ¦ Relays @ Bluebell ¦
ATSI-2019-081 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2236 |  | Maysville 69 kV Bus Protection | FirstEnergy has identified protection schemes on networked lines and buses using a certain vintage of relays that have a history of misoperation. Schemes protecting these facilities have no local backup so failures impact a larger portion of the system. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦¦ - 081 ¦ Maysville 69 kV Bus Protection ¦ 143 / 143 ¦ 153 / 184 ¦ Relays @ Maysville ¦
ATSI-2019-082 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2237 |  | North Star BlueScope Steel Customer- Need | Existing Customer Connection - Load Increase An existing transmission customer (North Star BlueScope Steel) is requesting load demand increase for the existing 345/34.5 kV substation to a new peak of 300 MVA on the Fulton-North Star Steel 345 kV line. Requested In-Service Date: 03/01/2021 The customer is also requesting load demand increase for its existing 138/34.5 kV substation to a new peak load of 40 MVA on the Delta-Wauseon 138 kV line. Requested In-Service Date: 11/01/2020
ATSI-2019-083 | ATSI | PJM West | 2019-11-22 | 2020-02-21 |  |  |  | Harding - Jennings 138 kV lines | Existing Customer Connection - Service Modification - The existing customer requested modification to their current 138 kV transmission service. - The request is to move some of their existing load from the Harding - Jennings Q13 138 kV line to the Harding - Jennings Q11 138 kV line. This request is not for a load increase, but will result in a system topology change. Requested In-Service Date: 02/01/2020
ATSI-2019-084 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2238 |  | Maclean 138 kV Substation - Need | Maclean 138 kV Substation - Breakers and Protection Schemes Breakers B132203 and B13204 Oil Circuit Breakers (OCB) are at/beyond expected service life (greater than 30 years) with increasing maintenance concerns; severe hydraulic leaks, oil quality issues, and increasing maintenance trends. The electromechanical relays provide limited bus protection with single point of failure. The bus PTs are at/beyond expected service life (greater than 40 years).
ATSI-2019-085 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2239 |  | Cedar Street 138 / 69 kV Substation - Need | Cedar 138/69 kV Street Substation - Breakers, Relays, and Control Building Breaker B-26 69 kV Bus Tie Breaker and disconnect switches are at/beyond expected service life (greater than 52 years) with increasing maintenance concerns; deteriorated operating mechanism, spare part availability, and increasing maintenance trends. North and South bus PTs are deteriorating and at/beyond expected service life (greater than 40 years). Transformer 138/69 kV #1, bus protection, and line exit relays are electromechanical and prone to misoperation. Cedar Street - Shenango 138 kV Line Cedar Street - New Castle 138 kV Line Cedar Street - New Castle #1, #2 and #3 69 kV Lines Cedar Street - Frisco #1 and #2 69 kV Lines Cedar Street - McDowell 69 kV Line Cedar Street - Grant Street 69 kV Line Cedar Street - New Wilmington 69 kV Line Cedar Street - Lowellville North 69 kV Line Cedar Street - Lowellville South 69 kV Line Cedar Street - Columbiana 69 kV Line
ATSI-2019-086 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2240 |  | Fowles and Pleasant Valley 138 kV Substation - Need | Fowles 138 kV Substation - Breaker and substation equipment Breaker B-8 Oil Circuit Breaker (OCB) is at/beyond expected service life (greater than 60 years) with increasing maintenance concerns; hot spots, oil leaks, and increasing maintenance trends. CTs and disconnect switches are at/beyond expected service life. Relays are electromechanical and prone to misoperation Pleasant Valley 138 kV Substation - Breakers and Substation Equipment Breaker B-1 Oil Circuit Breaker (OCB) is at/beyond expected service life (greater than 30 years) with increasing maintenance concerns; hot spots and deteriorated oil within the tank, deterioration of terminal block wiring in the cabinet. CTs and disconnect switches are at/beyond expected service life.
ATSI-2019-087 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2241 |  | Cloverdale Substation - Need | Cloverdale Substation - Breakers, Relays, and Control Building The transformer 138/69 kV relaying is electro-mechanical and is prone to misoperation. The substation disconnects D264, D262, D195, D193 and D192 have deteriorating blades and jaws. Transformer Breaker B-191 Oil Circuit Breaker (OCB) is aging greater than 30 years with increasing replacement concerns
ATSI-2019-088 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2242 |  | Maple-Pine 69 kV Line & Pine Substation- Need | Maple-Pine 69 kV Line The existing 69 kV transmission line is approximately 18 miles long with approximately 45 MWs of load and 11,500 customers at risk. The largest customer and load base at risk is located at Mars substation (22 MWs / 5,300 Customers). Overall line condition is adequate based on recent line inspection results. System performance over the past five years: 5 momentary / 6 sustained Pine 69 kV Substation - Breakers and Protection Schemes Several SF6 breakers at Pine substation at/beyond expected service life with increasing maintenance concerns; Breaker B-18 has history of SF6 leaks Breaker B-14 has history of SF6 leaks and has had air tank issues Breaker B-22 has experienced a bushing failure and repairs Breaker B-26 has had a bushing, air receiver, pilot valve and a lower pressure cut-off valve issues The transfer line and bus protection electro-mechanical relays are prone to mis-operate due to components failing without warning.
ATSI-2019-091 | ATSI | PJM West | 2019-11-22 | 2020-03-19 | 2020-06-08 | S2243 |  | Fowles and Pleasant Valley 138 kV Substation - Need | Fowles 138 kV Substation - Breaker and substation equipment Breaker B-8 Oil Circuit Breaker (OCB) is at/beyond expected service life (greater than 60 years) with increasing maintenance concerns; hot spots, oil leaks, and increasing maintenance trends. CTs and disconnect switches are at/beyond expected service life. Relays are electromechanical and prone to misoperation Pleasant Valley 138 kV Substation - Breakers and Substation Equipment Breaker B-1 Oil Circuit Breaker (OCB) is at/beyond expected service life (greater than 30 years) with increasing maintenance concerns; hot spots and deteriorated oil within the tank, deterioration of terminal block wiring in the cabinet. CTs and disconnect switches are at/beyond expected service life.
ATSI-2020-024 | ATSI | PJM West | 2020-08-14 |  |  |  |  | Eastlake-Lloyd 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-001 | ATSI | PJM West | 2020-01-17 | 2020-05-22 | 2020-10-01 | S2265 |  | Streetsboro 69 kV Area Need | Streetsboro 69 kV Substation and System Configuration Streetsboro is a straight 69 kV bus with no breakers or interrupting devices. The Ravenna-Lake Rockwell- 69 kV line (approximately 7.59 miles) is a radial line; normally open point near Streetsboro substation. Customers and load at risk: Approximately 5,000 customers / 25 MWs
ATSI-2020-002 | ATSI | PJM West | 2020-02-21 | 2020-04-20 | 2020-07-02 | S2246 |  |  | Richland-East Leipsic 138 kV (~15.8 miles) Transmission Line: • The Richland-East Leipsic 138kV Transmission Line was built in the 1960s. The average age of the structures on this line are 54 years old. FirstEnergy has historically experienced an average age of reject for wood poles to be 48.7 years. • Line was surveyed in 2018 and showed a structure reject rate of 100% (126/126). The primary reasons for reject were structure age, woodpecker holes, pole top decay, and phase raised structures. • There has been a growing trend in unscheduled interruptions on this line. There have been 11 total outages since 2011 for lightning, equipment failures, and other issues. • There has been an increase in unplanned maintenance on this line. A recent aerial patrol found 90 active maintenance conditions requiring repair for wood pole rot, broken static wire and attachment hardware, and bent braces.
ATSI-2020-003 | ATSI | PJM West | 2020-04-21 | 2020-05-22 | 2020-10-01 | S2264 |  | Magellen | New Customer Connection – A customer requested 138 kV transmission service for approximately 95 MVA of total load near the Highland-GM Lordstown 138 kV Line.
ATSI-2020-028 | ATSI | PJM West | 2020-08-14 |  |  |  |  | Midway - Richand - Wauseon | Midway-Richland-Wauseon 138kV (~33.5 miles) Transmission Line:  Existing 336.4 ACSR has a history of failure due to conductor vibration resulting in thermal overload and corrosion of steel core.  Original porcelain insulators from 1948 construction are aged and exhibiting wear.  Comprehensive aerial inspection was completed in 2020 and shows a rising negative trend in required maintenance with 160 structures that presently require repair for structure damage, static wire damage, broken insulators, and broken or overheated conductor.  Growing trend in unscheduled interruptions on this line with five (5) equipment caused outages in the past 10 years.  Condition of static wire is deteriorating which may be contributing to rise in lightning caused outages.
ATSI-2020-029 | ATSI | PJM West | 2020-08-14 |  |  |  |  | Napoleon-Richland-Stryker | Napoleon-Richland-Stryker 138kV (~32 miles) Transmission Line:  Existing 336.4 ACSR has a history of failure due to conductor vibration resulting in thermal overload and corrosion of steel core.  Existing line is constructed on double circuit lattice towers shared with the MidwayRichland-Wauseon 138kV line.  Comprehensive aerial inspection was completed in 2020 and shows a rising negative trend in required maintenance with 130 structures that presently require repair for worn static wire, damaged attachment hardware, and broken or flashed insulators.  Growing trend in unscheduled interruptions on this line with six (6) equipment caused outages in the past 10 years.
ATSI-2020-030 | ATSI | PJM West | 2020-08-14 |  |  |  |  | Napoleon-Richland-Stryker tap | Napoleon-Richland-Stryker 138kV, Tap to Ridgeville (~1.5 miles):  Tap was originally constructed in the 1970s. The average age of structures on this line are 50 years old. FirstEnergy has historically experienced an average age of reject for wood poles to be 48.7 years.  41 of 45 wood pole structures on this tap were bypassed during a previous project on the main line in 2015. Line survey in 2018 determined that all 41 structures failed. The primary reasons for reject were wood pole cracking and decay.  Both the entrance and exit to Ridgeville substation share the same structures, increasing risk to reliability.
ATSI-2020-031 | ATSI | PJM West | 2020-08-14 |  |  |  |  | Maysville - Mcdowell 69 | Maysville-McDowell 69kV Line (~33 miles):  Line was originally constructed in the 1960s. The average age of structures on this line are 54 years old. FirstEnergy has historically experienced an average age of reject for wood poles to be 48.7 years.  Line survey in 2019 showed a structure reject rate of 86% (528 of 613). The primary reasons for reject were woodpecker holes, wood pole decay, and pole top extensions previously used to mitigate the issue of pole top rot, an indicator that the pole is deteriorating.  Conductor condition is deteriorating with over 40 conductor splices in a 30 mile line section.  Obsolete line switches (A-2092, A-2091, A-2143 N.O.) are no longer supported by the manufacturer  Line has experienced eleven (11) outages in the past five years of which eight (8) are sustained.
ATSI-2020-032 | ATSI | PJM West | 2020-08-14 |  |  |  |  | Dilsworth-Maysville 69 | Dilworth-Maysville 69kV (~11.4 miles) Transmission Line:  Line was originally constructed in 1947. The average age of structures on this line are 58 years old. FirstEnergy has historically experienced an average age of reject for wood poles to be 48.7 years.  Line survey in 2019 showed a structure reject rate of 57% (166 of 293). The primary reasons for reject were wood pole deterioration, broken static wire, woodpecker holes, broken conductor strands.  Existing 336.4 ACSR has a history of failure due to conductor vibration resulting in thermal overload and corrosion of steel core.  Environmental conditions on ROW causes difficulties for routine maintenance, vegetation management, and outage restoration.  Growing trend in unscheduled interruptions with 10 outages in the past two years with approximately 15,000 customers impacted in the area.  Obsolete line switch (A-212 N.O.) is no longer supported by the manufacturer.
ATSI-2020-033 | ATSI | PJM West | 2020-08-14 |  |  |  |  | Bluebell - Knox 69 | Bluebell-Knox No1 69kV (~16 miles) Transmission Line:  Original H-frame wood pole construction dating back to 1970s.  Line survey in 2020 showed a structure reject rate of 92% (242 of 262). The primary reasons for reject were large woodpecker holes, wood pole decay, and pole top extensions previously used to mitigate the issue of pole top rot, an indicator that the pole is deteriorating.  Obsolete line switches (A-6935 & A-6936) are no longer supported by the manufacturer.  Growing trend in unscheduled interruptions with six (6) equipment caused outages in the past 5 years for cross-arm failures and pole failures; Outages have historically had a large impact on customers interrupted and customer minutes interrupted.
ATSI-2020-004 | ATSI | PJM West | 2020-04-21 | 2020-06-19 | 2020-10-16 | s2294 |  | Marusy | Masury 138 kV Substation System analysis shows that after a Masury 138 kV bus fault, a substantial amount of load is at risk (~42 MW) Masury 138 kV bus fault ATSI-P1-2-OEE-138-024 outages five 138 kV lines, two 138/69 kV transformers, and two 138-23 kV transformers There have been five pre-contingency switching events in the past year for the Masury 23 kV area Five (5) 138 kV OCB breakers (B2, B85, B101, B87, and B6) at Masury are showing end of life characteristics; Deteriorated bushings Deteriorated mechanism Oil leaks Age (>30 years) with increasing maintenance Obsolescence of equipment and spare parts Masury 138 kV bus protection currently employs a bus blocking scheme which is not the FE standard protection scheme
ATSI-2020-039 | ATSI | PJM West | 2020-11-20 |  |  |  |  | Lincoln Park | McGraw Edison oil circuit breakers B-67, B-68, and associated disconnect switches at Lincoln Park are experiencing increasing maintenance concerns; hydraulic fluid issues, deteriorated operating mechanisms and increasing maintenance trends.  Breakers B-67 and B-68 are 48 years old  Associated terminal equipment line arrestors and substation conductor
ATSI-2020-040 | ATSI | PJM West | 2020-09-11 |  |  |  |  | Victoria Rd | New Customer Connection - A customer requested 69 kV transmission service for approximatly 4.2 MVA of total load near the Kimberly-Salt Springs 69 kV line
ATSI-2020-044 | ATSI | PJM West | 2020-11-20 |  |  |  |  | Henrietta-Johnson 69 | Henrietta-Johnson 69 kV Transmission Line is approximately 16 miles in length. Line survey in 2020 showed a structure reject rate of 43% (93 of 218). The primary reasons for reject were wood pole deterioration, woodpecker holes, ground system damage, and decay damage. Worst performing transmission circuit in ATSI. Growing trend in unscheduled interruptions with 20 equipment failure caused outages in the past 5 years which have historically impacted approximately 9,200 customers. The majority of outage causes are related to Failed AC Circuit Equipment (conductor, crossarm, static wire, insulator, etc.). Transmission line switches are obsolete and limiting the transmission line rating.
ATSI-2020-045 | ATSI | PJM West | 2020-11-20 |  |  |  |  | Sharon 69 |  The 69 kV lines at the Sharon 69 kV substation have a single set of relays providing protection.  The Sharon 69 kV bus has a single bus protection scheme.  There is no breaker failure presently installed on the Sharon 69 kV exposing this sub and its lines to risk of a larger outage if one of these schemes were to fail to operate.  In June 2018, an uncleared fault on Y-300 line to McDowell led to a widespread outage of all the 69 kV lines from Sharon.
ATSI-2021-003 | ATSI | PJM West | 2021-01-15 |  |  |  |  | East Archbold-Stryker 69 kV New Customer | New Customer Connection – A customer requested 69 kV transmission service for approximately 5.6 MVA of total load near the East Archbold – Stryker 69 kV line.
AEP-2021-AP002 | AEP | PJM West | 2021-01-15 |  |  |  |  | Buchanan County, Virginia | Line Name: Dismal River – Grundy – Looney Creek 69kV Original Install Date (Age): 1935 Length of Line: ~8.8 mi Total structure count: 64 Original Line Construction Type: Wood Conductor Type: 3/0 ACSR, 336,400 ACSR, 556,500 ACSR, 795,000 ACSR Momentary/Permanent Outages and Duration: 6 Momentary and 1 permanent Outage CMI (last 5 years only): 339,660 minutes Line conditions: Dismal River – Grundy – Looney Creek 69kV: 13 structures with at least one open condition, 20% of the structures on this circuit. 16 structure related open conditions: woodpecker holes in poles, rot top crossarms, rot top poles, and a broken knee / vee brace. 1 open condition related to broken guy wire. 13 of 64 structures are 1930s vintage, 20% of the structures on this circuit. 18 of 64 structures are 1970s vintage, 28% of the structures on this circuit. Twenty Mile Switch Station creates a three terminal line with no ability to sectionalize.
ATSI-2020-005 | ATSI | PJM West | 2020-04-21 | 2020-09-11 |  | s2388 |  | Boardman - Sammis 138 | Boardman-Sammis 138 kV Line The Nevada substation serves 42 MW and 5,729 customers via the Boardman-Sammis 138 kV Line. The P1-2 contingency (ATSI-P1-2-OEE-138-024) for the loss of the Boardman-Sammis 138 kV Line will outage roughly 42 MW and 5,729 customers. Boardman-Sammis 138 kV Line has experienced seven outages in the past five years (two sustained) Circuit limiting substation conductor located at Nevada substation for both the Boardman-Nevada and Nevada-Sammis 138 kV circuit
ATSI-2020-006 | ATSI | PJM West | 2020-04-21 | 2020-05-22 | 2020-10-01 | S2261 |  | Abbe - Johnson #1 | Abbe – Johnson #1 69 kV switch (A-47) Switch originally installed in 1982 Corrosion on operating mechanism Existing KPF switch is obsolete and no longer supported by the manufacturer Undesirable design with vertical operating rod Transmission line ratings are limited by the existing switch rating
ATSI-2020-007 | ATSI | PJM West | 2020-05-22 | 2020-07-17 | 2020-10-16 | S2297 |  | East Akron 138 kV | Substation Condition Rebuild/Replacement  Increasing negative trend in maintenance findings and/or costs  Expected service life (at or beyond) or obsolescence Add/Expand Bus Configuration  Loss of substation bus adversely impacts transmission system performance  Eliminate simultaneous outages to multiple networked elements under N-1 analysis  Capability to perform system maintenance
ATSI-2020-008 | ATSI | PJM West | 2020-05-22 | 2020-07-17 | 2020-10-16 | S2298 |  | Barberton 138 kV | Barberton 138 kV configuration and condition:  Barberton 138 kV substation is a main and transfer bus configuration substation  A fault on the bus or between the bus and the circuit breaker or a failure of a single circuit breaker or a failure of a relay to trip will result in an outage of the entire bus or substation interrupting five 138 kV lines and two 138-23 kV transformers Deteriorating control building and substation equipment:  The control house was built in 1927, 93 years old.  Does not have space for new cables and additional panels.  The cables from the 138 kV yard run through an older tunnel under the railroad property to the control house in the distribution yard. The cables in the tunnel can’t be removed because they are encased in mineral deposits.  The control house has the panels on the second story and poses a challenge to replace and/or maintain the panels.
ATSI-2020-009 | ATSI | PJM West | 2020-04-20 | 2020-06-19 | 2020-10-16 | S2295 |  | Boardman - Lowellville 69 kV | New Customer Connection – A customer requested 69 kV transmission service for approximately 9 MW of total load near the Boardman-Lowellville # 2 69 kV Line.
ATSI-2020-010 | ATSI | PJM West | 2020-05-22 | 2020-06-19 | 2020-10-16 | S2296 |  | Cedar Street - New Castle 138 kV | New Customer Connection – A customer requested 138 kV transmission service for approximately 10 MW of total load near the New Castle-Cedar Street 138 kV Line.
ATSI-2020-014 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Gallion 138/69 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-015 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Masury-Maysville 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-016 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Babb |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-017 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Highland-Mahnningside 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-018 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Highland-GM Lordstown |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-019 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Dale - West Canton 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-020 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Dale-South Akron 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-021 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Avery-Shinrock 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-022 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Central-Packard 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-023 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Wauseon-Delta 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-025 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Cardington 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-026 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Brookside-Longview East 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-027 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Hanna - West Ravenna 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
ATSI-2020-034 | ATSI | PJM West | 2020-08-14 | 2020-11-20 |  |  |  | Masury-Maysville 138 |  FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation.  Proper operation of the protection scheme requires all the separate components perform adequately during a fault  In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology.  Transmission line ratings are limited by terminal equipment.
AEP-2021-AP003 | AEP | PJM West | 2021-01-15 |  |  |  |  | Smyth County, VA | APCo Distribution has requested a new station to be served from the Broadford — Richlands 138 KV line. The projected peak demand is 21 MW.
AEP-2021-AP004 | AEP | PJM West | 2021-01-15 |  |  |  |  | Smyth/Tazewell County, VA | Saltville — Tazewell 138 KV (installed in 1927) Length: ~21 Miles Original Construction Type: Lattice Steel Original Conductor Type: 97.3% 397.5 ACSR, 1 % 795 ACSR, 1.5% 1033.5 ACSR Momentary/Permanent Outages: 15/2 (5 years) Total structure count: 98 Number of open conditions: 26 Open conditions include: broken conductor strands, broken/burnt insulators. Unique structure count with open conditions: 12 (12%) Additional Info on Insulator & Hardware Corrosion: Section Loss: The connecting elements including the tower attachment hole and the insulator hook have experienced serious cross-section loss due to corrosion and wear. This loss of metal cross-section significantly reduces the capacity of the connection Corrosion: The insulator caps and connecting hardware have experienced heavy to complete loss of galvanizing. When the protective galvanized coating is gone or significantly compromised, the bare steel corrodes at an accelerated rate Tower members with corrosion and damage. Lattice tower structures have little structural redundancy. A failure of one member of the structure will impact the integrity of the structure and may cause the entire tower to collapse.
AEP-2021-OH001 | AEP | PJM West | 2021-01-15 |  |  |  |  | Canton, Ohio | Equipment Material/Condition/Performance/Risk: The Wagenhals 138-69-23kV station was originally constructed in 1943. The station directly serves approximately 140 MW of industrial load (130 MW steel mill at 138kV; 10 MW casting plant at 23kV).138kV breaker ‘H’ has routine SF6 leaks and 138kV breaker ‘A’ has an oil leak. There are 3- 69kV oil-filled breakers (P, Q, S), installed between 1962-1970, that are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling requirements. In addition, spare parts or technical support for these breakers are not available. This model of breakers has been prone to hydraulic mechanism malfunctions. The 2- 23kV breakers are oil-filled and were installed in 1977. These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. In addition, spare parts or technical support for these breakers are not available. This model of breakers has been prone to hydraulic mechanism malfunctions. There are a large number of 69kV and 23kV transmission hook-stick switches identified in need of replacement with Gang Operated Air-Breaker Switches (GOAB) The 138kV & 23kV PT’s are original to the station (1943) and have significant rusting and are at risk of oil spills. The station contains 103 electromechanical relays and 1 static relay. These relays have significant limitations with regard to spare part availability, SCADA functionality, and fault data collection and retention. In addition, these relays lack vendor support. The relays of concern are involved with 138kV, 69kV, & 23kV circuit protection, 69kV & 23kV bus protection, and transformer protection. The 138-23kV transformer #1 (vintage 1957) has the following asset concerns: insulation breakdown, elevated levels of CO2, high moisture readings, leaks, and wood-tie foundations in poor condition. The 138-69-23kV transformer #2 (vintage 1967) has the following asset concerns: insulation breakdown, elevated ethane and ethylene levels, high moisture readings, and low dielectric strength, and wood-tie foundations in poor condition. The control house has various issues: water intrusion, animal-related damage, lead paint, leaking roof, and asbestos. The 23kV yard has corroded steel and crumbling foundations, along with cap-and-pin insulators. In addition, energized equipment does not meet current clearance requirements. There are environmental concerns: positive tests for PCB’s; lead paint and asbestos, which are a safety risk to field personnel. The ground grid is inadequate and the AC station service and DC cabinets are in very poor condition. All 3 station transformers lack an oil containment system. Operational Flexibility and Efficiency: The 3- transformers lack a high-side fault interrupting devices and require tripping an entire 138kV bus to clear a fault. These dissimilar zones of protection can cause over tripping and mis-operations. The 138kV design consists of 2- straight buses with a single bus-tie breaker, this configuration causes extended outages for maintenance, especially for a station serving a major steel customer. A stuck-breaker contingency on the 138kV bus-tie breaker requires tripping 9- 138kV breakers, 4- 69kV breakers, and 2- 23kV breakers (15 total breakers), taking the entire station out of service. This contingency would result in load loss of approximately 140 MW, loss of a 138kV cap bank, plus the loss of 2 sources to the local 69kV system.
AEP-2021-OH002 | AEP | PJM West | 2021-01-15 |  |  |  |  | Franklin County, OH | Customer Service: A customer has requested transmission service just south of AEP’s existing Parsons Station in Lockbourne, OH. The customer has indicated an initial peak demand of 100 MW with an ultimate capacity of up to 675 MW at the site.
APS-2020-003 | APS | PJM MA | 2020-04-16 | [5 empty] | Transmission line ratings are limited by terminal equipment: Burma –Piney 115 kV Line; System Condition Issues at Burma 115 kV terminal
COMED-2019-006 | COMED | PJM West | 2019-10-17 | 2019-11-22 | 2020-01-28 | S2137 |  | Quad Cities | 345 kV Line 0402 (Quad Cities – Cordova) has obsolete relays. Becoming difficult to service REL352 phase comparison relays. They are being phased out of our system. Line is an intertie between PJM/MISO.
Dayton-2020-005 | Dayton | PJM West | 3/19/2020, 4/20/2020 | [5 empty] | The NW portion of the Dayton transmission system has experienced several real-time performance events over the last 5 years as a result of aging infrastructure and legacy system design. The Coldwater to Rossburg 69kV line (6684) is ~28 miles long and was built in 1967 with wood poles. - The line provides transmission and distribution service to 4 tapped substations including 1 Dayton delivery point and 3 cooperative delivery points. The line serves approximately 3,500 customers representing approximately 30 MW of peak load. - This line has experienced 8 permanent outages and 23 momentary outages in the last 3 years. The most common outage cause was equipment failures, particularly on the Macedon tap and between Sharpsburg and Rose Hill. - DP&L has a related project in the vicinity, (s0326, s0327, and s0328), which would help provide a source into the NW system on the Coldwater-Rossburg 6684 line. The Celina-Coldwater-Rockford 69kV line (6688) is ~23 miles long and was constructed in 1990 with wood poles and crossarm design. - The 6688 line provides service to 2 delivery points, serving approximately 1,900 customers and 12 MW of peak load. - This line has experienced 10 permanent and 12 momentary outages since 2016, with the primary causes being equipment failure and weather. - Dayton has a normally open 33kV tie (3339) with Ohio Power at Rockford Sub that is built to 69kV standards. This is an out of phase tie point and can only be closed if the 12kV Rockford bus is de-energized and 3339 line is energized from Ohio Power. Since this is a normally open point, the Rockford load is radial under most operating conditions since a manual process must take place to switch the load to the Ohio Power source if there is an issue with the Celina- Coldwater-Rockford 6688 69kV line. - The Rockford Substation is one of the most remote areas on the Dayton system and lacks nearby sources. The Amsterdam-Coldwater 69kV line (6629) is ~17 miles long and was constructed in 1991 with wood poles and crossarm design. - The line provides transmission and distribution service to 3 tapped substations including 1 Dayton delivery point and 2 cooperative delivery points. The line serves approximately 3,500 customers representing approximately 18 MW of peak load. - This line has experienced 6 permanent outages and 8 momentary outages since 2016. The most common outage causes were equipment failures and weather. DP&L provides 69kV service to the City of Celina from a very small 69kV switching station. This legacy design has a single point of failure that has become problematic for equipment maintenance and outages. - The peak load for the City of Celina is ~43 MW. - A bus or line fault on Celinas system interrupts both of the 69kV deliveries to Celina. - Due to the size of the switching station, there is very limited ability to expand or improve the configuration.
COMED-2019-007 | COMED | PJM West | 2019-10-17 | 2019-11-22 | 2020-01-28 | S2138 |  | Kendall - Lockport | Network project n5144 is rebuilding 345 kV Kendall – Lockport double circuit towers for 16 miles in 2022 to increase line 10805 rating. New conductor will be T2-1113 (1448 MVA SN/1863 MVA SE). 345 kV Line 10806 runs in parallel on the same towers. Existing conductor is 2156 kcm(1334 MVA SN/1726 MVA SE). The disconnect switch at Lockport is a non-standard 1600 A switch. 138 kV lines 0908 (Joliet – Shorewood) and 9117 (Shorewood – Cargo Court) run along the same ROW for 10.5 miles on wood poles. The wood poles are 59-60 years old. ComEd intends to eliminate wood poles on the transmission system.
Dayton-2020-007 | Dayton | PJM West | 2020-06-19 |  |  |  |  | Russells Point, Ohio | The Bellefontaine-Blue Jacket-Indian Lake 6648 69kV transmission line is a 16 mile three-terminal line located in Logan County, Ohio. The line features wooden cross-arm and post construction designs. The 6648 line provides service to customers served at 7 different substations: Indian Lake (DP&L), Huntsville (DP&L), Harrison (Logan REA), HBD Thermoid (DP&L), AGC Automotive (DP&L), Bellefontaine (DP&L), and Blue Jacket (DP&L). A fault on 6648 results in at least a momentary outage on 9 distribution transformers, 35MW of load, and possible sustained outages to the multitude of customers served from the line. Also, an outage on 6648 between the Blue Jacket tap and Harrison (Logan REA) will make the remaining circuit radial that provides service to Honda Transmission (Logan REA) and 10 other points of delivery served from the 6631 line in this configuration. The 6648 line has experienced 1 permanent and 3 momentary outages since 2017. The permanent outage was caused by a tree outside of the right of way and the momentary outages were caused by lightning, an issue on the distribution underbuild, and a failed piece of equipment during switching. The 6648 line serves approximately 35MW of load and has 16 miles of exposure (560MW-mile), although the line has performed well, there is significant exposure on this circuit that must be reduced to ensure long-term reliability. Immediately east of Indian Lake substation, the 6648 line crosses a low-lying area for approximately 0.75 miles. For several months of the year, structures are in standing water. Circuit 6906 is a radial line 2.0 mile long radial line connecting Indian Lake to a large industrial load (23 MW).
ComEd-2020-001 | ComEd | PJM West | 2020-03-10 | 2020-04-14 | 2020-06-15 | S2247 |  | Lisle Transformer 83 | Lisle 345/138 kV Transformer #83 acoustic testing shows higher than expected vibration levels and increased frequencies associated with looseness in the core/coil assembly. • Looseness has worsened since previous testing • Shell form design that cannot be re-blocked • Dissolved gas analysis shows insulation degradation. • Last unit of 5 that were purchased with this design. 3 of the 5 failed catastrophically and one other was condemned before failure.
ComEd-2020-002 | ComEd | PJM West | 2020-04-14 | 2020-05-12 | 2020-08-07 | S2266 |  | Itasca | Itasca 345 kV configuration does not comply with current standards. It is a straight bus design with four lines and two transformers with only two 345 kV circuit breakers, one of which is obsolete and has poor test scores. Two lines are connected directly to the bus with disconnect switches. Transformers do not have high side circuit breakers. 345 kV/138 kV Transformer 82 has partial discharge gassing due to a design deficiency and questionable acoustic test results. 2 out of 5 similar transformers have failed in service.
ComEd-2020-003 | ComEd | PJM West | 2020-04-14 | 2020-05-12 | 2020-08-07 | S2267 |  | Elmhurst | Elmhurst 345 kV configuration does not comply with current standards. It is a straight bus design with two 345 kV bus tie circuit breakers protecting two lines and three transformers. Lines and transformers are directly connected to the bus via switches. Lines and transformers trip together. Both 345 kV circuit breakers are obsolete and are in need of bushing replacements due to leaking oil.
Dayton-2020-011 | Dayton | PJM West | 2020-12-18 |  |  |  |  | Preble & Montgomery County, Ohio | Buckeye Power, on behalf of Darke Rural Electric Cooperative, has requested reliability upgrades on the West Manchester–Brookville 69kV 6639 and the West Manchester–Garage Road 69kV 6656 lines located in Preble and Montgomery Counties.
ComEd-2020-004 | ComEd | PJM West | 2020-04-14 | 2020-06-02 | 2020-09-15 | s2285 |  | McCook | McCook 345 kV bus does not comply with current standards. It is a straight bus design with two lines and two transformers with the lines directly connected to the bus via disconnects. Loss of a line also trips a transformer.
DEOK-2018-003 | DEOK | PJM West | 2018-11-29 | [5 empty] | New and existing industrial load growth in the area west of the Cincinnati/Northern Kentucky International Airport is predicted to exceed the capacity of the local distribution system. An additional 40MWs is requested.
DEOK-2019-001 | DEOK | PJM West | 2019-02-20 | [5 empty] | The distribution system feeding this area from Hebron and Limaburg is nearing its capacity limit. 70-90 MVA of load growth is expected in this area over the next five years. Duke Energy Distribution has requested a new transmission to distribution substation in the Petersburg, KY area.
DEOK-2019-004 | DEOK | PJM West | 2019-03-25 | [5 empty] | The painted lattice tower that supports the Miami Fort – Clifty Creek 138kV line has deep rust exhibiting heavy pack-out including deformed members and missing bolts. Concrete foundations are spalling causing exposure of reinforcing steel resulting in the delamination of concrete. Anchor bolts are rusting and as a result are showing significant section loss causing a reduction in tensile strength. Subsequent to this 86 year old tower’s installation adjacent to Miami Fort generation station a fly ash pond was built near it. The tower now sits in/on the dike between the fly ash pond and the Ohio River. The owner of the fly ash pond considers this high risk and has asked that the tower be moved off the dike. The condition of the tower combined with its use is also a risk. This tower is one side of the Ohio River crossing.
DEOK-2019-005 | DEOK | PJM West | 2019-03-25 | [5 empty] | Duke Energy Distribution has requested a new delivery point at Aicholtz substation. The two 69/13kV 10.5MVA transformers at Aicholtz are currently loaded to 86%. There are plans for new subdivisions and a new Medical Center in this area. Distribution Planning projects the transformers at Aicholtz will be loaded to 95% by 2020. Subsequent commercial development is expected.
ComEd-2020-005 | ComEd | PJM West | 2020-04-20 | 2020-05-22 | 2020-08-07 | S2268 |  | Line 15508 | 138 kV Line 15508 is a three terminal line. The current configuration is difficult to relay properly due to unequal lengths of the three legs. • Nelson (4.5 miles) • Dixon (5.7 miles) • Schauff Rd. (13.1 miles)
ComEd-2020-006 | ComEd | PJM West | 2020-04-20 | 2020-05-22 | 2020-08-07 | S2269 |  | Lines 0905/0906 | • 138 kV Line 0905 (Joliet – Hillcrest – Joliet Central – Weber Rd. – Will County), 15 miles total, has 2.4 miles of 300 kcmil cu conductor. Conductor was installed in 1942. • 138 kV Line 0906 (Joliet – Hillcrest – Joliet Central – Weber Rd. – ESS J332 tap – Will County), 16.5 miles total, has 3.0 miles of 300 kcmil cu conductor. Conductor was installed in 1942. • 300 cu conductor has iron clamps that cause heating issues • Attachments are made with aluminum clamps with a bi-metallic buffer between the clamps and the conductor which is difficult for the crews to handle.
DEOK-2019-024 | DEOK | PJM West | 2019-11-22 |  |  |  |  | Brighton 69/13kV substation | The City of Cincinnati is planning to replace the Western Hills Viaduct. The new roadway will be constructed immediately south of the existing roadway. Brighton substation is in the path of the new roadway. Brighton serves 40MW of residential, commercial and light industrial load with two 69/13kV 35MVA transformers connected to five feeder exits each.
ComEd-2020-007 | ComEd | PJM West | 2020-04-20 | 2020-07-17 | 2020-10-21 | s2349 |  | New Customer in Dekalb area | New customer has requested service in the Dekalb area • In service by 9/2021 with initial load < 5MW, growing to 200 MW by the end of 2026
ComEd-2020-008 | ComEd | PJM West | 2020-05-12 | 2020-07-07 | 2020-10-21 | s2350 |  | Kincaid SPS | To prevent first swing and/or oscillatory instability of either unit, a multi-phase fault high-speed sectionalizing scheme and a multiple line outage scheme are in place at Kincaid. 345 kV circuit breakers are all 1966 vintage and have had increased maintenance required over the past several years.
DEOK-2019-027 | DEOK | PJM West | 2019-11-22 |  |  |  |  | Elmwood 138/69/13 kV Substation | At Elmwood substation Duke Distribution is replacing switchgear on 13kv Bus 1 and 13kV Bus 2 with open air switches. Buses 1 and 2 presently have a single feed, the tertiary winding of 138/69/13kV 55MVA TB6. The transmission system is exposed to faults from five distribution feeders through this tertiary winding.
DEOK-2020-001 | DEOK | PJM West | 2020-02-21 |  |  |  | 2020-04-20 |  | A 69 kV feeder runs south from Buffington to a tap near Empire, from that tap to a second tap at Oakbrook and then to Limaburg. In the event of an interruption of the 138 kV feeder from Woodspoint to Aero, all load normally shared by both feeders is carried by the 69 kV feeder. Duke Distribution predicts load growth of 30 MW at Aero, 5 MW at Oakbrook and 5 MW at Limaburg by the summer of 2022. The higher loads plus the loss of the Woodspoint to Aero feeder lead to an overload of the tap to tap to Oakbrook section of the 69 kV feeder
ComEd-2020-009 | ComEd | PJM West | 2020-05-22 | 2020-06-19 | 2020-09-15 | s2286 |  | Bellwood | ComEd Distribution is replacing 138/34 kV transformer 78 at Bellwood which is currently tapped from 138 kV line 13501 (Elmhurst – Bellwood). The transformer and the line trip together.
DEOK-2020-004 | DEOK | PJM West | 2020-07-17 | [5 empty] | In the early 1960s Cincinnati Gas & Electric, Columbus & Southern Ohio Electric and Dayton Power & Light formed a joint venture to share the costs of building new power infrastructure. The construction of Stuart Station was one of the shared projects. In 2018 the joint venture was dissolved with the assets split among the companies. Duke Energy (formally CG&E) received the 138kV section of the substation at Stuart. Going into service in the early 1970s, this section of the substation has three circuit breakers connected to a straight bus, a 138/69kV transformer that is switch connected to an AEP feeder and a 345/138kV transformer that is switch connected to a DP&L 345kV bus. Duke Energy needs to isolate, protect and control its section of the substation. The breakers are oil filled and obsolete.
DEOK-2020-005 | DEOK | PJM West | 2020-10-16 |  |  |  |  | Clearcreek | Duke Energy Distribution has requested a new delivery point in Clearcreek Township, OH. This once rural area between Cincinnati and Dayton continues to see steady residential and commercial load growth of 2% per year. The load in this area is expected to exceed the capacity of the local distribution system by 2024.
DEOK-2020-006 | DEOK | PJM West | 2020-10-16 |  |  |  |  | Summerside | The 34 kV bus at Summerside is fed by two transformers. TB2 is a 138/69/34 kV transformer with breakers connections on the 138 and 69 kV buses and a switch connection to the 34 kV bus. TB5 is a 138/34 kV transformer with switch connections to the 138 and 34 kV buses. This arrangement exposes the transmission system to faults from the 34 kV system.
DEOK-2020-007 | DEOK | PJM West | 2020-10-16 |  |  |  |  | Central | At Central 69/13 kV transformers TB1 and TB2 both show excessive levels of acetylene and ethylene gasses indicating arcing, overheating and insulation breakdown.
DEOK-2020-008 | DEOK | PJM West | 2020-11-20 |  |  |  |  | Half Acre | Duke Energy Distribution has requested a new delivery point near Half Acre Road in Clermont County, OH. A new industrial customer has requested 36MW of distribution service by 10-01-2022. The new load exceeds the capacity of existing distribution facilities in the area.
ComEd-2020-010 | ComEd | PJM West | 2020-07-17 | 2020-08-14 | 2020-10-21 | s2353 |  | Load Addition in Burr Ridge Area | An existing customer has requested an additional 43 MW by 06/2022 with a total increase of 77 MW by the end of 2030.
DOM-2018-017 | DOM | PJM South | 2018-10-11 |  |  |  |  | Kingsboro | DENC Distribution has submitted a request for a new substation (Kingsboro) to serve two new customers located in Edgecombe County, North Carolina. DENC Distribution does not have distribution facilities in the area to serve this customer load request. The two customers request service, one by 7/1/2019 and the other by 1/15/2020.
ComEd-2020-011 | ComEd | PJM West | 2020-07-17 | 2020-08-14 | 2020-10-21 | s2354 |  | New Customer in Rochelle Area | Customer has requested new service by 12/2021 with a load of 20 MW.
ComEd-2020-012 | ComEd | PJM West | 2020-12-18 | 2021-01-15 |  |  |  | 138 kV BT 1-2 at ESS J310 | 4 Current Transformers on 138 kV BT1-2 breaker at ESSJ310 are failing and there is a risk of mis-operation or overtripping. Breaker age is 70 years old. Components are obsolete; therefore repair is impossible.
Dayton-2019-005 | Dayton | PJM West | 2019-02-20 | 2020-11-20 |  |  |  | Monroe Township, Ohio | - Existing distribution circuits AZ1210 and AZ1205 from Vandalia Substation exceeded their thermal rating this past summer. There continues to be strong load growth in this area with multiple transmission and distribution customer requests. - Distribution circuits that supply the growing load center emanate from distant substations and end-use customers are beginning to see voltage issues. Specifically this has been an issue on distribution circuit OC1204 from West Milton. - There are critical customers served in this area and there is a need to supply sufficient capacity and diversity to ensure continued reliable operations amid the rapid load growth.
Dayton-2019-009 | Dayton | PJM West | 2019-10-25 | 2019-12-18 | 2020-02-03 | S2150 |  | Brookville, Ohio | An new industrial customer has requested a new delivery point in Brookville, Ohio. The potential customer site is located north of Upper Lewisburg Salem Rd and west of Arlington Rd in close proximity to the existing 6639 transmission line. The route of the existing 6639 line is shown in the graphic on the right side of the slide.-Prior to the need for full transmission capacity, the customer will require 500kW of capacity immediately to begin construction activities. By April 1, 2020 the customer will require a minimum of 5MW of total capacity to finalize building construction and the installation of production equipment. By November of 2020, the full substation and capacity for an 11MVA load will be required. There are long-terms plan for the customer to potentially grow to a 26MVA load.-In order to support the customer’s delivery needs, support local economic development, and maintain system reliability for all customers, it is necessary to promptly begin designing and building a comprehensive solution that can supply the customer needs and meet the schedule outlined in this slide.
Dayton-2019-010 | Dayton | PJM West | 2019-12-18 | 2020-03-19 | 2020-05-13 | S2210 |  | Sidney, Ohio | An industrial customer served from the Sidney substation intends to add 10 MVA of load in 2020 Q3. All three of the 69/12 kV transformers at Sidney substation are already loaded to ~90% during peak times. The loss of one of the three 69/12 kV transformers
Dayton-2020-001 | Dayton | PJM West | 2020-02-21 | 2020-04-20 | 2020-06-19 | S2254 |  | Russia, Ohio | The existing 42 mile 69kV transmission line (6625) from Covington-Minster-Rossburg was constructed using wood pole, cross-arm and brace design in 1971. This line provides transmission and distribution level service to 6 different substations serving nearly 7,000 customers in Darke, Mercer, Miami, and Shelby Counties in Ohio and totaling approximately 40MW of load. – A fault occurring anywhere on this 42 mile line will result in at least a temporary outage and potential permanent outage to all 7,000 customers. -This line is one of the worst performing 69kV transmission lines in the Dayton zone. The line has experienced 30 outages (5 permanent and 25 momentary) since 2016, and the total duration of those outages is ~3700 minutes. Most of the permanent outages have been caused by equipment related issues while most of the momentary outages have been the result of weather. -This is a three-terminal transmission line which causes protection and control concerns which could lead to possible misoperation. There are existing sectionalizing switches to help reduce outage time but the switches have not operated reliably during outage conditions and will need addressed.
Dayton-2020-002 | Dayton | PJM West | 2020-03-19 | 2020-04-20 | 2020-06-19 | S2255 |  | Jasper, Ohio | The existing 32 mile 69kV transmission line (6636) from Xenia-Glady Run-Jamestown was constructed using wood pole, cross-arm and brace design in 1929, with some replacements made in 1951. This line provides transmission and distribution level service to five different substations serving approximately 8,000 customers in both Greene and Clark Counties in Ohio. - A fault occurring anywhere on this 32 mile line will result in at least a temporary outage and possibly a permanent outage to 6 distribution transformers and all 8,000 customers served from the 6636 line. This line is one of the worst performing 69kV transmission lines in the Dayton zone. The line has experienced 13 outages (3 permanent and 10 momentary) since 2016, and the total duration of those outages was ~900 minutes. Most of the permanent outages were caused by auto accidents and animals, while most of the momentary outages were the result of weather. Large commercial and industrial distribution customers served from the five substations supplied by the 6636 line have experienced loss of supply events emanating predominantly from disturbances on the 6636 line. One particular industrial customer has experienced a total of 18 events (T&D) since 2016 but the majority of events have been related to 6636 transmission line performance. This is a three-terminal transmission line which causes protection and control concerns.
Dayton-2020-003 | Dayton | PJM West | 2020-03-19 | 2020-04-20 | 2020-06-19 | S2256 |  | Octa, Ohio | The existing 31 mile 69kV transmission line (6902) from Washington CH-Jamestown was constructed using predominantly wood pole, cross-arm and brace design in 1950. This line provides transmission and distribution level service to three different substations serving approximately 3,800 customers in both Greene and Fayette Counties in Ohio. - A fault occurring anywhere on this 31 mile line will result in at least a temporary outage and possibly a permanent outage to all 3,800 customers. This line is one of the worst performing 69kV transmission lines in the Dayton zone. The line has experienced 25 outages (7 permanent and 18 momentary) since 2016, and the total duration of those outages was ~1,719 minutes. Most of the permanent outages were caused by crossarm issues while most of the momentary outages were the result of weather. Large commercial and industrial distribution customers served from the three substations supplied by the 6902 line have experienced loss of supply events emanating predominantly from disturbances on the 6902 line. There are limited distribution switching capabilities out of Jeffersonville Sub since there are no nearby distribution substations located close to the load center.
Dayton-2020-004 | Dayton | PJM West | 2020-03-19 | 2020-04-20 | 2020-06-19 | S2257 |  | Jackson Center, Ohio | - The Village of Jackson Center is planning to add load and has constructed a second substation. The Jackson Center Municipal load is currently tapped off the Jackson Center-Indian Lake 6614 69kV transmission line in the northern part of Daytons service territory. - The Jackson Center-Indian Lake 69kV transmission line is approximately 13 miles long and was constructed in 1955 with wood poles and crossarm design, which is prone to weather related outages. - This line has experienced 3 permanent outages and 3 momentary outages since 2016, with the majority of causes being equipment failure (static wire, breaker, phase down). A line fault results in an outage to the entire Village with no ability to transfer load. - The point of interconnection for Jackson Center municipal is only 575 feet from Daytons Jackson Center Substation. There is a switch that can be operated to sectionalize the line towards Indian Lake.
Dayton-2020-006 | Dayton | PJM West | 2020-03-19 | 2020-10-16 |  |  |  | North Dayton Zone | The Amsterdam-Shelby 138kV transmission line (13827) is approximately 26 miles long and was constructed in 1974 with wood poles. - A fault on any portion of this circuit will result in an outage to a large 55MW industrial customer. Permanent faults on the Shelby side of the line could lead to reduced capacity to serve load for an extended duration depending on system conditions. - The Amsterdam-Shelby 138kV line has experienced 2 permanent and 4 momentary outages since 2016. The permanent outages were caused by galloping conductors and an auto accident, while the momentary outages were caused by lightning and an animal. - The Amsterdam-Shelby 138kV line is critical in providing a 138kV source into the NW area of the DP&L transmission system. In this rural area, there are limited sources and an outage to this source combined with other area outages can lead to operational voltage and loading issues. This contingency is regularly trending in real-time operations and has occurred. Galloping conductors have been problematic in this area causing multiple 69kV outages over the past 2 years causing operational issues to surface. Transmission line equipment issues have been identified along the Amsterdam-New Bremen-St Marys 69kV line (6630) related to vintage cross-arm design and bracing of transmission poles at the base. - The 6630 line was constructed in 1970 and is ~8 miles long. - This line has experienced 2 permanent and 2 momentary outages since 2016. The majority of the outages were caused by equipment failure. - The Village of New Bremen has a peak load of ~20MW of load - This corridor serves as a key tie between the Ohio Power and Dayton systems in this area. The Village of Minster is served from two sources, the Covington-Minster-Rossburg 69kV line (6625) and the Amsterdam-Minster 69kV line (6672). During winter storm conditions and with galloping lines in this area, Minster has lost both transmission feeds. - The Village of Minster serves ~1,500 customers and has a peak load of ~25MW of load. - The 6672 line is ~1.7miles long and is 1970s cross-arm design and ties into the strongest area source at Amsterdam Sub. - The 6672 line has experienced 5 outages, 4 momentary and 1 permanent, since 2016. The majority of the outages were caused by weather, including the permanent outage which was the result of galloping conductors. -
Dayton-2020-008 | Dayton | PJM West | 2020-07-17 | 2020-10-16 |  |  |  | Fayette County, Ohio | • Buckeye Power, on behalf of South Central Power, has requested a new transmission delivery point in Fayette County, Ohio. • The primary function of this new delivery point will be to serve existing load that is presently being served from another substation roughly 12 miles away. • The proposed delivery point is located immediately east of DP&L’s Washington CourthouseGreenfield 69kV (6649) transmission line. • Washington Courthouse and Greenfield substations are shown in Figure 1 where the 69kV lines are marked in green and the approximate location of the new delivery point is highlighted with a yellow star on the map. • Initial loading of the proposed delivery point is projected to be 3 MW and emergency loading could be up to 5MW. • Service to the new delivery point is required by June 2022.
Dayton-2020-009 | Dayton | PJM West | 2020-10-16 | 2020-12-18 |  |  |  | Dayton, Ohio | Historically Dayton assumed a 50/50 current split in our ratings methodology. Under certain outage conditions, lines or transformers may be isolated on a single element with 100% of the flow through that facility. After reviewing industry best practices, DP&L plans to move from a 50/50 current split assumption to a 100/0 current split assumption starting January 1, 2023. Modeling single elements derates in the planning model is in implementation and will require contingency change updates in the future, but modeling these specific scenarios in the operations model was not a feasible long-term plan for DP&L. Certain terminal equipment changes will be made at DP&L substations to maintain current ratings and other facilities will take the derate from the change in methodology based on reviews of historical loading, contingency loading, and criticality as reviewed by planning and operations. The decision to proceed with the changes was driven by the desire to avoid unplanned facility outages due to potential loading issues and the low cost of making terminal equipment upgrades to avoid these scenarios.
Dayton-2020-010 | Dayton | PJM West | 2020-11-20 | 2021-02-17 |  |  |  | North Dayton Zone | • Buckeye Power, on behalf of Pioneer Rural Electric Cooperative, has requested reliability upgrades on the Staunton-KTH 69kV 6657 line located in Miami and Champaign Counties. • The 6657 line is a radial 17-mile 69kV wood pole line connecting DPL’s Staunton Substation to Pioneer’s KTH delivery point. • The line was constructed primarily in the 1960’s and is approximately 17 miles long. • The line has experienced 2 permanent and 3 momentary outages since 2016. Most outages were caused by lightning. • The line serves approximately 19MW of load between East Casstown, St. Paris, and KTH substations. • Loss of the 6657 line could lead to extended customer outages for customers served via East Casstown, St. Paris, and KTH due to the current radial configuration and limited switching options. • The KTH delivery point served at the end of the radial 6657 line provides service to the largest employer in Champaign County.
Dayton-2020-012 | Dayton | PJM West | 2020-12-18 | 2021-02-17 |  |  |  | Dayton, Ohio | A large new senior community featuring a mix of residential and retail is being constructed in the Cornerstone Development located in Centerville, OH. This area, served from Dayton’s Carpenter Substation, has experienced growth in recent years and this load addition of 5MVA will require additional capacity. Dayton must develop a solution to have capacity to serve distribution load in this load center or risk overloading existing equipment and not having sufficient distribution capacity to serve growing load.Carpenter Substation is served via a short 0.1 mile tap from the Alpha-Hempstead 6622 69kV transmission line. Carpenter Substation provides distribution service to the 3,4000 customers served in this area via a single 69/12kV 30MVA transformer. A single outage to the 6622 transmission line or distribution transformer at Carpenter would result in a complete loss of service to the 3400 customers. The current load (24.4 MVA) and reserved emergency switching capacity (3.5 MVA) place the current 69/12kV 30MVA transformer at Carpenter above 90% of its rating during peak times before the 5MVA load addition. Additional circuit ties exist in the area but do not have enough capacity for significant load transfers and would further limit the ability to conduct circuit switching during outages.
DEOK-2019-020 | DEOK | PJM West | 2019-07-24 | 2020-03-19 | 2020-05-13 | S2211 |  | Locust - Fairfield | Buckeye Power, on behalf of Butler Rural Electric Cooperative, has requested Duke Energy review options for improving the reliability of the 34 mile long, 69 kV circuit from Fairfield to Locust substations. The six BREC delivery points connected to the circuit serve 5,135 customers and experienced 7,015,437 customer minutes of interruption (CMI) in the 2009-2019 YTD period [data provided by Buckeye Power]. Duke Energy’s Stillwell and River Circle substations serve 3,130 customers and experienced 4,596,672 CMI in the 2009-2019 YTD period.
DEOK-2019-023 | DEOK | PJM West | 2019-11-22 | 2020-01-17 | 2020-03-02 | S2180 |  | Wyscarver – Merrell Dow | The 69kV feeder from Wyscarver to Marion Merrell Dow is in deteriorating condition. Constructed in 1940 with wooden mono poles and cross arms, and 300 and 400 kcmil copper conductor, 18% of the 101 structures were rejected and 12 open conditions were reported during a recent inspection. The line has had one momentary and eight sustained outages in the last five years with 5,042 customers experiencing an average outage time of 574 minutes.
DEOK-2019-025 | DEOK | PJM West | 2019-11-22 | 2020-01-17 | 2020-03-02 | S2181 |  | Clermont, Beckjord | Clermont substation is one of three sources of supply to the far eastern 69 kV system serving large portions of Clermont and Brown Counties. The vintage 1950’s substation is in deteriorating condition. Structural steel is rusting. Concrete footings are starting to crack and spall. There are 138kV & 69kV cap and pin insulators which are prone to failure. Clermont has two 138/69kV 33MVA transformers. TB1 was manufactured in 1953. TB2 was manufactured in 1962. Both transformers continue to show increasing levels of gassing. Elevated levels of acetylene indicate internal problems. Doble testing indicates the insulation on the windings is deteriorating. Ground switches are used as high side protective devices. This old design causes a fault on the 138kV system when they operate, interrupting the 138kV Circuit from Beckjord to Summerside. If there is a fault on a transformer or bus it could result in a sustained outage to the 138kV circuit, effectively causing all of Clermont substation to be de-energized. It is impossible to install high side circuit switchers as protective devices and 138kV line switches for sectionalizing due to the configuration of the substation. To do this would require a complete substation rebuild. The hillside site is too small to reconfigure or rebuild to current standards.
DEOK-2019-026 | DEOK | PJM West | 2019-11-22 | 2020-01-17 | 2020-03-02 | S2182 |  | Fairfield 138/69/34 kV Substation | At Fairfield substation 138/34kV 56MVA TB1 is showing high levels of dissolved combustible gasses, especially acetylene indicating arcing in this 54 year old transformer. 138/69/34kV TB2’s tertiary winding is connected to a grounding transformer and a 34kV distribution bus. This old system design exposes the transmission system to greater risk due to faults on the distribution system.
DEOK-2020-003 | DEOK | PJM West | 2020-07-17 | 2020-11-20 |  |  |  |  | A customer fed by Meadow substation is expecting a 10MW load increase by the summer of 2022. Meadow has two incoming 69kV feeders, one from Trenton and a normally opened one from Yankee-Jackson via the tap to Meadow. If the feeder to Trenton is opened Meadow throws over to the feeder from the tap. In this state the additional 10MWs of customer load will drive the Yankee to Meadow tap section of the feeder to 106% of its emergency rating.
DOM-2020-0008 | DOM | PJM South | 2020-04-14 | [5 empty] | Dominion Energy has identified a need to replace approximately 160 ft of conductor at Everetts Substation on Line#2014 Earleys – Everetts to improve system performance and increase line capacity. This short segment of conductor is imposing a limit on the remaining sections of the line.
DEOK-2020-008 | DEOK | PJM West | 2020-11-20 | 2021-01-15 |  |  |  | Half Acre | Duke Energy Distribution has requested a new delivery point near Half Acre Road in Clermont County, OH. A new industrial customer has requested 36 MW of distribution service by 10-01-2022. The new load exceeds the capacity of existing distribution facilities in the area.
DOM-2019-020 | DOM | PJM South | 2019-05-16 | 2019-10-17 | 2020-02-24 | s2129 |  | Enterprise 230 kV Delivery – Add 3rd TX – DEV | DEV Distribution has submitted a DP Request to add a 3rd, 84 MVA distribution transformer at Enterprise Substation in Loudoun County. The new transformer is being driven by continued datacenter load growth and alternate feed contract reservations. Requested in-service date is 07/15/2020. Note: Distribution’s Customer is also requesting 145 MVA of alternate capacity.
DOM-2019-022 | DOM | PJM South | 2019-05-16 | 2019-10-17 | 2020-02-24 | s2130 |  | Poland Road 230kV Delivery- Add 4th TX - DEV | DEV Distribution has submitted a DP Request to add a 4th, 84 MVA distribution transformer at Poland Road Substation in Loudoun County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the xisting transformers. Requested inservice date is 12/31/2021.
DOM-2019-023 | DOM | PJM South | 2019-05-16 | 2019-10-17 | 2020-02-24 | s2131 |  | Brickyard 230kV Delivery - DEV | DEV Distribution has submitted a DP Request for a new substation (Brickyard) to support a new datacenter campus in Prince William County with a total load in excess of 100 MW. Requested in-service date is 12/15/2021.
DOM-2019-024 | DOM | PJM South | 2019-10-17 | 2019-11-14 | 2020-02-24 | s2132 |  | Poland Road 230kV Delivery- Add 5th TX - DEV | DEV Distribution has submitted a DP Request to add a 5th, 84 MVA distribution transformer at Poland Road Substation in Loudoun County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers. Requested in-service date is 10/15/2022. Initial In-Service Load: Summer 268.0 MW Projected 2024 Load: Summer 293.0 MW
DOM-2019-025 | DOM | PJM South | 2019-07-11 | 2020-02-11 | 2020-11-04 | s2320 |  | Coleman Creek 115kV DP - MEC | ODEC has submitted a request on behalf of Mecklenburg Electric Coop (MEC) for a new delivery point (Coleman Creek) at Boydton, VA, to support a new datacenter campus with a total load in excess of 100 MW. The customer requests service by August 1, 2020.
DOM-2019-026 | DOM | PJM South | 2019-08-27 | 2019-10-21 | 2020-02-24 | s2133 |  | Dawsons Crossroads 115kV Delivery - DEV | NCEMC has submitted a request on behalf of Halifax EMC (HEMC) for a new Delivery Point (Dawsons Crossroads) at Halifax, NC, to replace an existing distribution Delivery Point due to poor reliability. The customer requests service by November 1, 2020.
DOM-2019-027 | DOM | PJM South | 2019-07-11 | 2020-02-04 | 2020-11-04 | s2319 |  | Chickahominy TX #1 Replacement - THA | Chickahominy 500-230 kV 840 MVA transformer #1 needs to be replaced as a result of Dominion’s ongoing transformer health assessment (THA) process. This process considers design characteristics, past electrical test results, dissolved gas-in-oil test results, age, ongoing maintenance issues, and past failures of similar designed transformers. This transformer was manufactured in 1987 and is the last Westinghouse shell transformer on the Dominion System, these transformers have known issues. Drivers for replacement are: * Reduced BIL Ratings * Previously remanufactured following failure * Transformers of this manufacture are considered suspect due to previous transformer failures
DOM-2019-028 | DOM | PJM South | 2019-10-17 | 2019-11-14 | 2020-02-24 | s2134 |  | Mt. Storm 2nd GIS Building | Ice and weather continue to be an issue at Mt Storm Substation that affects the operation and maintenance of the remaining outdoor equipment located in the substation. In 2014 half the existing 500 kV substation equipment was converted to GIS.
DOM-2019-030 | DOM | PJM South | 2019-09-24 | 2019-10-21 | 2020-02-24 | s2135 |  | Lexington TX#4 Replacement - DEV | Lexington Tx#4 is a 168 MVA 230/115 kV transformer originally manufactured by Ferranti Packard in 1986. This transformer is being replaced as part of our strategic transmission transformer replacement program as based on the results of our ongoing transformer health assessment (THA) process. Detailed drivers are: DGA indicates trending upward levels of Hydrogen, Methane, along with high levels of carbon monoxide and carbon dioxide since 1997. Oil was degasified in 2009 but gas trending continues. Reduced BIL ratings
DOM-2019-031 | DOM | PJM South | 2019-09-24 | 2019-10-21 | 2020-02-24 | s2136 |  | Gordonsville TX#3 Replacement - DEV | Gordonsville Tx#3 is a 224 MVA 230/115 kV transformer originally manufactured by Cooper Power Systems in 1990. This transformer is being replaced as part of our strategic transmission transformer replacement program as based on the results of our ongoing transformer health assessment (THA) process. Detailed drivers are: Transformer failed in service at Dooms in 1999, repaired / remanufactured in 2000 and returned to service in Gordonsville in 2005. Oil DGA indicates trending upward levels of Methane and Ethylene, along with high levels of carbon monoxide and carbon dioxide since returning to service. Reduced BIL ratings
DOM-2020-0001 | DOM | PJM South | 2020-02-04 | 2020-03-10 | 2020-11-04 | s2321.1 |  | Cloverhill 230kV Delivery- Add 3rd TX - DEV | DEV Distribution has submitted a DP Request to add a 3rd, 84 MVA distribution transformer at Cloverhill Substation in Prince William County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers. Requested in-service date is 06/01/2022.
DOM-2020-0003 | DOM | PJM South | 2020-03-10 | 2020-05-12 | 2020-11-04 | s2324.1 |  | Aviator Substation | DEV Distribution has submitted a DP Request for a new substation (Aviator) to accommodate a new datacenter campus in Loudoun County with a total load in excess of 100MW. Requested in-service date is 6/01/2023.
DOM-2020-0004 | DOM | PJM South | 2020-04-14 | 2020-05-12 | 2020-11-04 | s2321.2 |  |  | DEV Distribution has submitted a DP Request to add a 3rd, 84 MVA distribution transformer at Winters Branch Substation in Prince William County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers.
DOM-2020-0005 | DOM | PJM South | 2020-04-14 | 2020-05-12 | 2020-11-04 | s2321.3 |  |  | DEV Distribution has submitted a DP Request to add a 4th, 84 MVA distribution transformer at Winters Branch Substation in Prince William County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers.
DOM-2020-0006 | DOM | PJM South | 2020-03-10 | 2020-05-12 | 2020-11-04 | s2325 |  | North Anna Station 500kV Breaker Replacements | North Anna Station 500 kV Breakers 57302 & H602 are live tank breakers with external CTs and continue to have ongoing reliability issues. They were built in 2002. No internal breaker condition monitoring is available with these type of breakers.
DOM-2020-0007 | DOM | PJM South | 2020-03-20 | 2020-04-16 | 2020-11-04 | s2322 |  |  | The two ground switch/MOAB schemes protecting Buena Vista transformers #1 and #2 need to be replaced to prevent transformer operations from impacting adjacent Rockbridge and James Lee Substations • The two 800A wave traps located outside of Buena Vista Substation on structures 26/215A and 26/215B need to be replaced due to age (25 years) • A single span (approx. 625’) of 721 ACAR between structures 26/214 and 26/215 at Buena Vista Substation is the most limiting element affecting the rating of Line #26
DOM-2020-0009 | DOM | PJM South | 2020-03-20 | 2020-04-16 | 2020-11-04 | s2323 |  |  | A 115kV line switch at Berkley substation has been identified with operating issues. This switch on Line #51 is in-operable.
DOM-2020-0010 | DOM | PJM South | 2020-04-14 | 2020-05-12 | 2020-11-04 | s2326 |  |  | Section 56-585.1:5 of the Virginia Code, which was enacted as part of the 2018 Grid Transformation and Security Act was amended recently by the General Assembly of Virginia and signed into Law by the Governor on March 4th 2020 to allow for additional projects to qualify for the underground transmission line pilot program authorized therein. Pursuant to this amendment, a Customer and Fairfax County have requested that the Company relocate a portion of Transmission Line #2010 between Spring Hill substation and Tysons Substation underground to enable construction of a planned mixed use development which currently encroaches on the existing overhead transmission line
DOM-2020-0011 | DOM | PJM South | 2020-04-16 | 2020-05-21 | 2020-11-04 | s2327 |  |  | Dominion Energy has identified a need to replace Line #36 wave trap and arresters at Buggs Island NUG Substation due to end of life.
DOM-2020-0012 | DOM | PJM South | 2020-05-12 | 2020-06-02 | 2020-11-04 | s2328.1 |  |  | DEV Distribution has submitted a DP Request to add a 3rd, 112 MVA distribution transformer at Waxpool Substation in Loudoun County. The new transformer is being driven by continued load growth in the area.
DOM-2020-0013 | DOM | PJM South | 2020-05-12 | 2020-06-02 | 2020-11-04 | s2329.1 |  |  | DEV Distribution has submitted a DP Request for a new substation (Lincoln Park) to accommodate a new datacenter campus in Loudoun County with a total load in excess of 100MW.
DOM-2020-0034 | DOM | PJM South | 2020-09-10 | [5 empty] | Dominion Energy has identified a need to replace 42 wood pole structures (Churchland – Hodges Ferry segment) of Line# 87 (Churchland – Chesapeake Energy Center) based on the Company’s End of Life criteria. The 5.21 miles segment of Line# 87 was constructed on wood H-frame structures in 1957, and includes ACSR conductor and 3#8 static. These structures are at the end of their useful life. Industry guidelines indicate equipment life for wood structures is 35-55 years, conductor and connectors are 40-60 years, and porcelain insulators are 50 years. Line# 87 provides service to Bower’s Hill and Hodges Ferry substations with approximately 18 MW and 61 MW tapped load. Removal of the Churchland - Hodges Ferry segment will create a radial line exceeding Dominion’s 700 MW-miles criteria.
DOM-2020-0014 | DOM | PJM South | 2020-07-16 | 2020-08-13 | 2020-11-04 | s2337 |  |  | The 26 line extends 20.82 miles between Lexington to Balcony Falls. The 7.63 mile section between Balcony Falls and Buena Vista was constructed primarily on Blaw Knox structures in 1928 and includes ACSR conductor and 3#6 static. Industry guidelines indicate equipment life for wood structures is 35-55 years, conductor and connectors are 40-60 years, and porcelain insulators are 50 years. Within this section there are 18 structure locations that need to be replaced due to condition which makes up more than 21.7% of the segment structures. Removing this segment of Line#26 from service creates a violation of Dominion Energy's TP criteria whereby the loading on the resulting radial transmission line exceeds 700MW-Mile exposure limit
DOM-2020-0015 | DOM | PJM South | 2020-05-21 | 2020-06-16 | 2020-11-04 | s2330 |  |  | Remington CT Tx#9 is a 224MVA, 230/115kV transformer originally manufactured in 1971 as a 200 MVA unit and remanufactured in 1996 as a 224 MVA unit. This transformer is being replaced on the results of our ongoing transformer health assessment (THA) process. Oil DGA levels are trending upwards. Unit was exhibiting upward trending combustible gasses from 2001 to 2013 when oil was reprocessed, however gasses are continuing to trend upward even after oil processing. Reduced BIL ratings
DOM-2020-0016 | DOM | PJM South | 2020-05-21 | 2020-06-16 | 2020-11-04 | s2331 |  |  | DEV Distribution has submitted a DP Request to add a 3rd, 56 MVA distribution transformer at Taussig Substation in the City of Norfolk. The new transformer is being driven by new load from the Hampton Road Bridge Tunnel (HRBT) expansion. Requested in-service date is 05/31/2021.
DOM-2020-0040 | DOM | PJM South | 2020-11-04 | [5 empty] | DEV Distribution has submitted a DP Request for a new substation (Wakeman) to accommodate a new datacenter campus in Prince William County with a total load in excess of 100MW.
DOM-2020-0017 | DOM | PJM South | 2020-05-21 | 2020-06-16 | 2020-11-04 | s2332 |  |  | DEV Distribution has submitted a DP Request to add a 2nd, 33.6 MVA distribution transformer at Mercury Substation in the City of Hampton. The new transformer is being driven by new load from the Hampton Road Bridge Tunnel (HRBT) expansion.
DOM-2020-0042 | DOM | PJM South | 2020-11-18 | [5 empty] | Dominion Energy has identified a need to replace approximately 3.7 miles of 115kV Lines #53 and #72 between Chesterfield Power Station and the Brown-Boveri Tap, including an additional approximately 0.52 mile tap line into Kingsland Substation from Line #72.Mainly double-circuit, wood, 3-pole H-frame construction with structures dating back to 1956. ACSR conductor.January 2020 condition assessment indicated severe corrosion of the 3/8” steel static wire and woodpecker damage to a number of poles.Industry guidelines indicate equipment life for wood structures is 35-55 years, conductor and connectors are 40-60 years, and porcelain insulators are 50 years.
DOM-2020-0043 | DOM | PJM South | 2020-11-04 | [5 empty] | DEV Distribution has submitted a DP Request for a new substation (Park Center) to accommodate a new datacenter campus in Fairfax County with a total load in excess of 100MW
DOM-2020-0044 | DOM | PJM South | 2020-11-04 | [5 empty] | Dominion Energy has identified a need to replace 12 existing transmission towers that carry 230kV Lines #204 (Jefferson St-Gum Springs) and #220 (Ox-Gum Springs). The 12 towers include structures 204/29 to 204/40 and are located along an approximately 1.75 mile section of right-of-way between the Gum Springs tap and Belvoir Substation. The need for replacement is based on the Company’s End of Life criteria. The structures identified for replacement are CORTEN lattice-type towers that were constructed in 1966 and have reached the end of their useful life. 11 of the towers are double circuit structures while structure 204/40, located at the Gum Springs tap, is a triple circuit structure. Both lines, #204 and #220, provide service to Belvoir Substation and Gum Springs Substation with approximately 83 MW and 113 MW of tapped load, respectively.
DOM-2020-0019 | DOM | PJM South | 2020-09-01 | 2020-11-04 |  |  |  |  | DEV Distribution has submitted a DP Request for a new substation (King and Queen) to replace the source to an island of load that will be lost when a river crossing is eliminated as part of the 230kV Line #224 (Lanexa-Northern Neck) rebuild project
DOM-2020-0020 | DOM | PJM South | 2020-06-16 | 2020-07-16 | 2020-11-04 | s2333 |  |  | DEV Distribution has submitted a DP Request to add a 2nd, 12.5 MVA distribution transformer at St. Johns Substation in the Caroline County. The new transformer is needed to mitigate load loss for a transformer contingency
DOM-2021-0001 | DOM | PJM South | 2021-01-06 | [5 empty] | DEV Distribution has submitted a DP Request for a new substation (Youngs Branch) to accommodate a new datacenter campus in Prince William County with a total load in excess of 100MW
DOM-2020-0021 | DOM | PJM South | 2020-07-07 | 2020-08-04 | 2020-11-04 | s2328.2 |  |  | DEV Distribution has submitted a DP Request to add a 4th distribution transformer at Pacific Substation in Loudoun County. The new 112MVA transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers.
DOM-2021-0004 | DOM | PJM South | 2021-01-06 | [5 empty] | With the removal of temporary 230-115kV Bremo TX#7, Dominion Energy Operations Engineering has identified a potential overload on 230-115kV Bremo TX#9 for the loss of Line #2193 (Bremo-Fork Union). The identified overload occurs under the following conditions:System load at 11,000MW Bath County operating in pumping mode Bear Garden running at full output The overload is likely to occur every evening when Bath County is operated in pumping mode, forcing Bear Garden output to be curtailed.
DOM-2021-0006 | DOM | PJM South | 2021-03-09 | [5 empty] | Dominion Energy has identified a need to replace 52 double-circuit wood pole structures from Skiffes Creek to C&O Junction of Line #209 (Skiffes Creek-Yorktown) and Line #58 (Skiffes Creek-Yorktown), and 47 single-circuit wood pole structures from Structure 58/305 to Yorktown of Line #58 based on the Company’s End of Life criteria. The 6.2 miles segment from Skiffes Creek-C&O Junction of Line #209 and Line #58, and the 4.5 miles segment from Structure 58/305-Yorktown of Line #58 were constructed on wood H-frame structures in 1952 and includes ACSR conductor and 3#8 static. These structures are at the end of their useful life. Industry guidelines indicate equipment life for wood structures is 35-55 years, conductor and connectors are 40-60 years, and porcelain insulators are 50 years. Line #209 and Line #58 provide service to Lebanon substation with approximately 46.6MW of load. Line #58 provides service to Yorktown Naval Weapons station with approximately 6.5MW of load.
DOM-2021-0007 | DOM | PJM South | 2021-03-09 | [5 empty] | Dominion Energy has identified a need to replace five (5) existing double-circuit COR-TEN® lattice towers that carry Line #238 (Structure #4 to # 8) and Line #249 (Structure #88 to #92) based on the Company’s End of Life criteria. The five (5) transmission COR-TEN® towers were built in 1972 (49 years in service). The structures were noted to be subject to extensive deterioration. Continued degradation of the steel components and connections on these towers has severely reduced their structural integrity. Industry guidelines indicate equipment life for wood structures is 35-55 years, conductor and connectors are 40-60 years, and porcelain insulators are 50 years. A 50-year cycle for COR-TEN® steel structures is often cited. Line 238 serves 20.5 MW of directly connected load. Line 249 serves 20 MW of directly connected load and 24.1 MW load at Locks Sub.
DOM-2021-0008 | DOM | PJM South | 2021-03-09 | [5 empty] | Dominion Energy has identified a need to replace six existing COR-TEN® lattice tower structures from Carson to Poe Line #2002 from Structure #05 to #10 based on the Company’s End of Life criteria.Line 2002 runs approximately 12.58 miles from Carson to Poe. The six (6) transmission COR-TEN® towers were built in 1977 (44 years in service). The structures were noted to be subject to extensive deterioration. Continual deterioration of the steel components and connections on these towers has severely reduced their structural capacity and poses risk to the reliability of Line #2002. Industry guidelines indicate equipment life for wood structures is 35-55 years, conductor and connectors are 40-60 years, and porcelain insulators are 50 years. A 50-year cycle for COR-TEN® steel structures is often cited. Line 2002 serves 78 MW of loads at Poe Substation.
DOM-2021-0009 | DOM | PJM South | 2021-02-09 | [5 empty] | ODEC has submitted a request with an updated load projection on behalf of Mecklenburg Electric Coop (MEC) for a delivery point (Cloud Sub - Coleman Creek DP) at Boydton, VA, to support a datacenter campus with a total load in excess of 100 MW
DOM-2021-0010 | DOM | PJM South | 2021-02-09 | [5 empty] | ODEC has submitted a request on behalf of Mecklenburg Electric Coop (MEC) for a new delivery point (Easters Sub – Timber DP) at Boydton, VA, to support a new datacenter campus with a total load in excess of 100 MW.
DOM-2021-0011 | DOM | PJM South | 2021-02-16 | [5 empty] | DEV Distribution has submitted a DP Request to add a 2nd, 22.4 MVA distribution transformer at Chase City Substation in Mecklenburg County. The new transformer is needed to mitigate load loss for a transformer contingency
DOM-2020-0022 | DOM | PJM South | 2020-07-07 | 2020-08-04 | 2020-11-04 | s2328.3 |  |  | DEV Distribution has submitted a DP Request to add a 3rd distribution transformer at Cumulus Substation in Loudoun County. The new 84 MVA transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers.
DOM-2020-0023 | DOM | PJM South | 2020-07-07 | 2020-08-04 | 2020-11-04 | s2335 |  |  | DEV Distribution has submitted a DP Request to add a 6th distribution transformer at Dulles Substation in Fairfax County. The new 84 MVA transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers
DOM-2020-0024 | DOM | PJM South | 2020-07-07 | 2020-08-04 | 2020-11-04 | s2336 |  |  | DEV Distribution has submitted a DP Request to add a 4th distribution transformer at Waxpool Substation in Loudoun County. The 84 MVA new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers
BE-2019-0002 | BE | PJM MA | 2019-03-25 | [5 empty] | Westport to Center 115 kV underground transmission line requires relocation to support external customer work. The cables have also been identified for replacement for various issues including movement of splices, corrosion of parts, gassing, availability of spare materials and specialized resources.
DOM-2020-0025 | DOM | PJM South | 2020-06-16 | 2020-07-16 | 2020-11-04 | s2334 |  |  | DEV Distribution has submitted a DP Request for a new substation (Main Post) to serve existing load (<100 MW) at Fort Lee Army Post in Prince George County. The Army has requested the new substation (on their property) to isolate their load from the regulated 13.2 kV circuits fed by Fort Lee Substation and will bear the full cost of the project
DOM-2020-0026 | DOM | PJM South | 2020-08-04 | 2020-09-01 |  |  |  |  | NOVEC has submitted a DP Request for a new substation (Rollins Ford) to accommodate a new datacenter campus in Prince William County. NOVEC has requested a 230kV ring bus connection. Since the total load requested is less than 100 MW, NOVEC will be required to pay excess facilities for all equipment required for the ring bus configuration above a T-tap
DUQ-2020-001 | DUQ | PJM West | 2020-06-19 |  |  |  |  | Pittsburgh, PA | Various landslides were found along the 138 kV transmission circuits Dravosburg – Carson (Z-71) and Carson – Bettis (Z-88) affecting towers #3640, #3641, #3642, and #3643. Due to the landslide close proximity to the towers, transverse cracking, and the geological weak soil layers, the existing towers are expected to be vulnerable to movement which can compromise their structural integrity.
DOM-2020-0027 | DOM | PJM South | 2020-08-04 | 2020-09-01 |  |  |  |  | Line# 233 switches 23339 and 23336 are less than 15 years and have operating issues. Multiple bottle failures, vertical pipe u-joints have broken multiple times, system control center's records show they are inoperable.
DOM-2020-0028 | DOM | PJM South | 2020-09-01 | 2020-11-04 |  |  |  |  | Dominion Energy has identified a need to replace 47 existing transmission towers (Staunton – Valley) of Line#293.
DOM-2020-0029 | DOM | PJM South | 2020-11-18 | 2020-12-16 |  |  |  |  | Dominion Energy has identified the need to replace 92 transmission towers on Line #14 between Fudge Hollow and the interconnect with AEP.Line #14 extends 14.94 miles to AEP territory from Fudge Hollow. AEP is fed radially from Fudge Hollow, most of the time.Existing structures are 1920's vintage Blaw Knox galvanized/painted towers. The line is at the end of its useful life (94 years old) and the ground line conditions of the structures range from fair to severe condition.
BG-2020-0001 | BG | PJM MA | 2020-02-04 | 2020-03-10 | 2020-05-19 | s2206 |  | Waugh Chapel | Four 230 kV oil filled circuit breakers at Waugh Chapel are at risk of poor performance, have environmental risks/concerns along with parts availability issues
BG-2020-0002 | BG | PJM MA | 2020-02-04 | 2020-03-10 | 2020-05-19 | s2207 |  | Raphael Road | Two 230 kV circuit breakers at Raphael Road are at risk of poor performance, have had defective parts along with parts availability issues
BG-2020-0003 | BG | PJM MA | 2020-02-11 | 2020-03-20 | 2020-05-19 | s2208 |  | Granite | Two 115 kV oil filled circuit breakers at Granite are at risk of poor performance, have environmental risks/concerns along with parts availability issues
BG-2020-0004 | BG | PJM MA | 2020-02-11 | 2020-03-20 | 2020-05-19 | s2209 |  | Harford-Perryman | The Harford-Perryman 115kV circuits 110617, 110618 are wood H-Frame circuits with poles dating back to the 1950’s with nearly every pole having significant material condition issues including degraded pole shafts, arms, tops, bird holes including those from Pileated Wood Peckers, degraded insulators and hardware etc
BG-2020-0005 | BG | PJM MA | 2020-04-14 | 2020-06-02 | 2020-09-22 | S2277 |  | Riverside substation | At BGE’s Riverside substation, significant switching steps and equipment outages are required to support planned outages of the 230kV 2344 circuit, 230-1 transformer or associated underlying 115kV equipment. In addition, for unplanned outages of the same equipment, there are multiple elements at both 230 and 115kV voltage levels that are automatically taken out of service in order to isolate the fault conditions
Dayton-2020-011 | Dayton | PJM West | 2020-12-18 |  |  |  |  | Preble & Montgomery County, Ohio | Buckeye Power, on behalf of Darke Rural Electric Cooperative, has requested reliability upgrades on the West Manchester–Brookville 69kV 6639 and the West Manchester–Garage Road 69kV 6656 lines located in Preble and Montgomery Counties.The 6639 line is a 20-mile 69kV wood pole line serving three Dayton substations (Brookville, Lewisburg, West Manchester), one Darke REA Delivery Point at West Sonora, and one 69kV industrial customer. Lewisburg & West Senora Stations are both served via a 3.2-mile tap from the 6639 line. The 6656 line is a 16-mile 69kV wood pole line built to 138kV standards connecting Dayton substations at Garage Road and West Manchester . Lewisburg & West Senora utilize a 4.61-mile 69kV tap from the 6656 line as a normally open tie for emergency situations. Due to protection limitations, this normally open tie cannot be closed in during normal operations.
Dayton-2020-012 | Dayton | PJM West | 2020-12-18 |  |  |  |  | Dayton, Ohio | A large new senior community featuring a mix of residential and retail is being constructed in the Cornerstone Development located in Centerville, OH. This area, served from Dayton’s Carpenter Substation, has experienced growth in recent years and this load addition of 5MVA will require additional capacity. Dayton must develop a solution to have capacity to serve distribution load in this load center or risk overloading existing equipment and not having sufficient distribution capacity to serve growing load. Carpenter Substation is served via a short 0.1 mile tap from the Alpha-Hempstead 6622 69kV transmission line. Carpenter Substation provides distribution service to the 3,4000 customers served in this area via a single 69/12kV 30MVA transformer. A single outage to the 6622 transmission line or distribution transformer at Carpenter would result in a complete loss of service to the 3400 customers. The current load (24.4 MVA) and reserved emergency switching capacity (3.5 MVA) place the current 69/12kV 30MVA transformer at Carpenter above 90% of its rating during peak times before the 5MVA load addition. Additional circuit ties exist in the area but do not have enough capacity for significant load transfers and would further limit the ability to conduct circuit switching during outages.
DPL-2019-0002 | DPL | PJM MA | 2019-06-28 | 2020-03-20 | 2020-11-04 | s2378 |  | Grasonville Substation | Grasonville Substation is in a deteriorated condition and has experienced flooding issues
DPL-2019-0003 | DPL | PJM MA | 2019-10-21 | 2020-03-20 | 2020-11-04 | s2378 |  | Queenstown Area Reliability | Customers in the Queenstown area historically experience poor service reliability due to high customer counts on feeders and minimal distribution automation capability. MD PSC has mandated that DPL improve reliability in the state.
DPL-2019-001 | DPL | PJM MA | 2019-01-25 |  |  |  |  | Mt. Pleasant to Townsend 138 kV line | Customer has requested a new 138 kV interconnection point off the Mt. Pleasant to Townsend 138 kV line due to load growth within the municipality
DPL-2020-001 | DPL | PJM MA | 2020-08-04 | 2020-09-01 | 2020-11-04 | S2355.2 |  |  | The 500kV 5015 line running from Red Lion Substation to the Hope Creek Nuclear Station (PSEG) has experienced 9 faults in a span of 10 years due to avian activity and lightning strikes, most recently occurring twice in April 2020. The line is currently protected by power line carrier and requires a more reliable method for fault detection and isolation to prevent possible overtrips. • Access to multiple towers can only be accomplished by boat, making faults more difficult to locate and detect, adding to the need for more accurate fault location methods • 5015 line is critical to the operation of the Hope Creek and Salem Generating plants.
JCPL-2019-008 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Atlantic - Red Bank (S1033) 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: substation conductor. * Before: 678 / 780 * After: 709 / 869
JCPL-2019-009 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Atlantic - Eaton Crest - Red Bank (T2020) 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: line relaying, line trap, substation conductor * Before: 678 / 780 * After: 709 / 869
JCPL-2019-010 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Pohatcong - West Wharton 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Line Relaying, Circuit Breaker, Line Trap, Substation Conductor * Before: 678 / 813 * After: 709 / 869
JCPL-2019-011 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Gillette - Traynor 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Line Relaying, Circuit Breaker, Line Trap, Substation Conductor * Before: 678 / 802 * After: 843 / 1011
JCPL-2019-012 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Greystone - West Wharton 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor, Current Transformer * Before: 678 / 813 * After: 709 / 869
JCPL-2019-013 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Raritan River - Werner 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Circuit Breaker, Substation Conductor, Line Relaying, Current Transformer * Before: 652 / 739 * After: 709 / 869
JCPL-2019-014 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Greystone - Portland 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor, Current Transformer * Before: 830 / 1000 * After: 910 / 1077
JCPL-2019-015 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Gillette - Traynor 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor * Before: 678 / 813 * After: 709 / 869
JCPL-2019-016 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
DOM-2020-0030 | DOM | PJM South | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2338 |  |  | Dominion Energy has identified a need to replace 16 existing transmission towers (Chesterfield – Enon segment) of Line#2049 (Chesterfield – Allied
DOM-2020-0031 | DOM | PJM South | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2339 |  |  | NOEVC has submitted a DP Request for a new substation (Sojourner) in Loudoun County with a total load in excess of 100MW.
DOM-2020-0032 | DOM | PJM South | 2020-09-10 | 2020-11-18 |  |  |  |  | Dominion Energy has identified a need to rebuild Line#1001 (Battleboro – Chestnut) based on the Company’s End of Life criteria. Line 1001 was constructed on predominately wood H-frame structures in 1959 from Battleboro to Chestnut (9.28 miles) . Industry guidelines indicate equipment life for wood structures is 35-55 years, conductor and connectors are 40-60 years, and porcelain insulators are 50 years. The Line #1001 provides service to Consolidated Diesel and Whitakers substations with approximately 6.0 MW and 8.3 MW tapped load.
DOM-2020-0033 | DOM | PJM South | 2020-09-10 | 2020-11-18 |  |  |  |  | Dominion Energy has identified a need to rebuild Line#1024 (Chestnut – South Justice Branch) based on the Company’s End of Life criteria. Line 1024 was constructed on predominately wood H-frame structures in 1959 from Chestnut to South Justice Branch (3.39 miles of 6.41 miles) . Industry guidelines indicate equipment life for wood structures is 35-55 years, conductor and connectors are 40-60 years, and porcelain insulators are 50 years. The Line #1024 provides service to Cox DP substations with approximately 14.0 MW of tapped load.
DOM-2020-0035 | DOM | PJM South | 2020-10-06 | 2020-11-04 |  |  |  |  | DEV Distribution has submitted a DP Request to add a 3rddistribution transformer at Farmwell Substation in Loudoun County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers.
DOM-2020-0036 | DOM | PJM South | 2020-10-06 | 2020-11-04 |  |  |  |  | Dominion Energy has identified a need to replace 60 concrete structures of Line #2007 (Lynnhaven – Thalia) based on the Company’s End of Life criteria. The 3.37 miles long line was constructed on concrete structures in 1970. These structures have developed significant structural concerns as they age. Every pole is experiencing hairline cracking at a minimum, and many of the poles have more advanced cracking that has exposed some of the interior reinforcing bars and cables. The cracks allow for significant water infiltration which can accelerate the deterioration of the concrete and cause rusting of the steel reinforcing components.
DOM-2020-0037 | DOM | PJM South | 2020-10-06 | 2020-11-04 |  |  |  |  | Dominion Energy has identified a need to replace 20 concrete structures (Structure 2019/21 – Thalia segment) of Line #2019 (Greenwich – Thalia) based on the Company’s End of Life criteria. The 1.17 miles segment of Line #2019 was constructed on concrete structures in 1970. These structures have developed significant structural concerns as they age. Every pole is experiencing hairline cracking at a minimum, and many of the poles have more advanced cracking that has exposed some of the interior reinforcing bars and cables. The cracks allow for significant water infiltration which can accelerate the deterioration of the concrete and cause rusting of the steel reinforcing components.
DOM-2020-0041 | DOM | PJM South | 2020-11-04 | 2020-12-01 |  |  |  |  | DEV Distribution has submitted a DP Request to add a 4th distribution transformer at Cumulus Substation in Loudoun County. The new 84 MVA transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing transformers.
JCPL-2019-017 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Atlantic - Smithburg 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor * Before: 678 / 813 * After: 709 / 869
JCPL-2019-018 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-019 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Chester - Glen Gardner 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor * Before: 650 / 817 * After: 709 / 869
JCPL-2019-020 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Gilbert - Glen Gardner 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Wave Trap, Line Relaying, Current Transformer, Breaker and Terminal Switches, Line Metering * Before: 815 / 923 * After: 1136 / 1311
JCPL-2019-021 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Chester - West Wharton 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor * Before: 650 / 817 * After: 709 / 869
JCPL-2019-022 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 260 / 416 (63% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Bernardsville – Long Lines 34.5 kV Line ¦44 / 47 ¦44 / 53 ¦Line Relaying, Substation Conductor ¦5.3 ¦ ¦Long Lines – Greater Crossroads 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦3.2 ¦ ¦Greater Crossroads – Merck 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦6.2 ¦
JCPL-2019-023 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 275 / 346 (79% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Gilbert – Bridgeton 34.5 kV Line ¦37 / 45 ¦37 / 45 ¦- ¦3.9 ¦ ¦Bridgeton – Frenchtown 34.5 kV Line ¦37 / 45 ¦37 / 45 ¦- ¦2.3 ¦ ¦Frenchtown – Frenchtown Solar 34.5 kV Line ¦39 / 48 ¦39 / 48 ¦- ¦4.6 ¦ ¦Frenchtown Solar – Rosemont 34.5 kV Line ¦39 / 48 ¦39 / 48 ¦- ¦3.5 ¦ ¦Rosemont – Alexauken 34.5 kV Line ¦39 / 48 ¦39 / 48 ¦- ¦4.5 ¦ ¦Alexauken – Rocktown 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦Line Relaying ¦2.0 ¦
JCPL-2019-024 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 181 / 383 (48% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Greystone – Davis 34.5 kV Line ¦66 / 79 ¦70 / 85 ¦Substation Conductor ¦2.2 ¦ ¦Davis – Alderney 34.5 kV Line ¦46 / 58 ¦46 / 58 ¦- ¦0.3 ¦ ¦Alderney – Tabor Tap 34.5 kV Line ¦46 / 58 ¦46 / 58 ¦- ¦0.3 ¦ ¦Tabor Tap – Morristown Tap 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦1.1 ¦ ¦Morristown Tap – Morris Plains Tap 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦0.2 ¦ ¦Morris Plains Tap – Morristown 34.5 kV Line ¦34 / 43 ¦34 / 43 ¦- ¦3.6 ¦ ¦Morris Plains Tap – Morris Plains 34.5 kV Line ¦41 / 52 ¦83 / 100 ¦Disconnect Switches ¦1.5 ¦ ¦Morristown Tap – Whippany ¦41 / 50 ¦41 / 50 ¦- ¦6.2 ¦
DOM-2020-0045 | DOM | PJM South | 2020-12-01 | 2021-02-09 |  |  |  |  | ODEC (on behalf of Prince George Electric Cooperative – PGEC) has submitted a DP Request to convert existing Garyville DP, in Prince George County, from a distribution sourced delivery to a transmission sourced delivery due to poor supplier reliability.
DOM-2020-0046 | DOM | PJM South | 2020-12-16 | 2021-01-14 |  |  |  |  | ODEC has submitted a DP Request (on behalf of REC) to add a 4th, 56 MVA distribution transformer at Brandy in the Culpeper County. The new transformer is needed to meet area load growth.
DOM-2021-0002 | DOM | PJM South | 2021-01-06 | 2021-02-09 |  |  |  |  | DEV Distribution has submitted a DP Request to add a 3rd transformer at Shellhorn Substation in Loudoun County. The new transformer is required to accommodate continued load growth in the area and support contingency loading for loss of one of the existing transformers
DOM-2021-0005 | DOM | PJM South | 2021-01-06 | 2021-03-09 |  |  |  |  | Northern Neck Tx#4 is a 168 MVA, 230/115kV transformer bank consisting of three single-phase units that were manufactured in 1987. This transformer bank has been identified for replacement based on the results of Dominion’s transformer health assessment (THA) process. Detailed drivers include:Age (>30 years old). Reduced BIL ratings (3 levels below standard). Oil DGA indicates high CO and CO2 levels in all three units; potential breakdown of dielectric paper insulation on main current carrying conductors inside the transformer. LTC design (in-tank) does not allow oil samples to be taken to determine condition of LTC; Sister unit LTC failed in 2014; All three LTC’s replaced but have periodic sync issues. THA score less than 80
JCPL-2019-025 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 182 / 257 (71% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, rot/decay, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Highlands – Sandy Hook 34.5 kV Line ¦37 / 38 ¦37 / 38 ¦- ¦1.1 ¦ ¦Sandy Hook Switch Point – Sandy Hook 34.5 kV Line ¦26 / 33 ¦37 / 38 ¦Substation Conductor ¦0.1 ¦ ¦Sandy Hook Switch Point – Sea Bright Switch Point 34.5 kV Line ¦37 / 38 ¦37 / 38 ¦- ¦2.4 ¦ ¦Sea Bright Switch Point – Monmouth Beach 34.5 kV Line ¦35 / 38 ¦35 / 38 ¦- ¦2.0 ¦ ¦Monmouth Beach – Long Branch 34. 5 kV Line ¦34 / 38 ¦34 / 38 ¦- ¦2.2 ¦
JCPL-2019-026 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 132 / 134 (99% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, rot/decay, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Gillette – Green Village 34.5 kV Line ¦41 / 50 ¦41 / 50 ¦- ¦5.7 ¦
DOM-2021-0012 | DOM | PJM South | 2021-02-09 | 2021-03-09 |  |  |  |  | NOVEC has submitted a DP Request for a new substation (Altair) to serve a data center complex in Loudoun County with a total projected load in excess of 100MW
JCPL-2019-027 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 155 / 322 (48% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, rot/decay, woodpecker holes, etc ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Traynor – Madison Switch Point 34.5 kV Line ¦39 / 50 ¦39 / 50 ¦- ¦1.5 ¦ ¦Madison Switch Point – Madison 34.5 kV Line ¦55 / 67 ¦55 / 67 ¦- ¦1.0 ¦ ¦Madison Switch Point – Academy 34.5 kV Line ¦35 / 44 ¦35 / 44 ¦- ¦3.6 ¦ ¦Academy – Okner 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦2.2 ¦ ¦Okner – Mount Pleasant 34.5 kV Line ¦38 / 49 ¦38 / 49 ¦- ¦1.1 ¦ ¦Mount Pleasant – Whippany 34.5 kV Line ¦41 / 49 ¦46 / 58 ¦Substation Conductor ¦1.5 ¦
JCPL-2019-028 | JCPL | PJM MA | 2019-04-11 | 2019-12-12 | 2020-11-11 | S2244 |  | Atlantic SVC | The Atlantic SVC has an increasing trend of outages and failures increasing maintenance needs.
JCPL-2020-001 | JCPL | PJM MA | 2020-03-20 | 2020-07-07 | 2020-10-16 | s2300 |  |  | Oyster Creek substation serves approximately 30,300 customers and 120 MW of load. Loss of the Oyster Creek #7 and #8 230-34.5 kV transformers results in a local voltage collapse with the Oyster Creek – Bamber Lake – Whitings (Q121) 34.5 kV line overloaded >125% of its 52 MVA SE rating.
JCPL-2020-002 | JCPL | PJM MA | 2020-06-16 | 2020-07-16 | 2020-10-16 | s2308 |  |  | New Customer Connection – A customer requested 34.5 kV service, anticipated load is 7 MW, location is near the Morris Park – Phillipsburg 34.5 kV line.
JCPL-2020-003 | JCPL | PJM MA | 2020-06-16 | 2020-07-16 | 2020-10-16 | s2309 |  |  | New Customer Connection – A customer requested 34.5 kV service, anticipated load is 4 MW, location is near the Larrabee – Point Pleasant 34.5 kV line.
JCPL-2020-004 | JCPL | PJM MA | 2020-07-07 | 2020-08-04 | 2020-10-16 | s2315 |  |  | Customer Connection – JCP&L Distribution requested to complete a 230 kV service connection in 2016 with an initial in-service date of June 2018. The anticipated load is 9 MW, location is at the existing Manchester 230-12.5 kV substation.
JCPL-2020-006 | JCPL | PJM MA | 2020-08-13 | 2020-09-10 |  |  |  |  | New Customer Temporary Connection – A customer requested temporary 34.5 kV service, anticipated load is 4 MW, location is near the Washington – Pohatcong 34.5 kV line.
JCPL-2020-007 | JCPL | PJM MA | 2020-08-13 | 2020-09-10 |  |  |  |  | New Customer Connection – An existing customer requested a second 34.5 kV service, anticipated load is 2 MW, location is near the Larrabee – Point Pleasant 34.5 kV line.
DUQ-2019-001 | DUQ | PJM West | 2019-02-20 | 2020-06-19 | 2020-08-13 | S2275 |  | Monroeville, PA | The Pennsylvania Turnpike Commission (PTC) has informed Duquesne Light Company (DLC) that it plans to construct an expressway from Jefferson Hills Borough to I-376 in Monroeville. The initial construction phases of this expressway begin in Jefferson Hills and end in the city of Duquesne. The construction of this expressway will closely follow the DLC transmission corridor between the Wilson and Port Perry transmission stations and, as such, a number of DLC’s existing transmission structures will be impacted and/or displaced. The PTC has requested that all DLC modifications are completed prior to the start of the corresponding expressway construction phase, the last of which is 3/31/2023.
DUQ-2020-002 | DUQ | PJM West | 2020-09-11 | 2020-10-16 |  |  |  | Springdale, PA | The existing #2-4 138kV bus tie and Z-56 Bus #2 breakers at Cheswick SS are ITE type 138KM breakers that were manufactured in 1968. ABB (who now owns the rights to ITE breakers) does not support this model breaker, which creates maintenance difficulties due the lack of available spare parts. Cheswick SS also contains two (2) 138kV capacitor banks. Substations with 138kV capacitor banks experience higher frequency current during faults, due to the contribution of the capacitors. Oil breakers are susceptible to damage from these higher frequency currents.
JCPL-2020-008 | JCPL | PJM MA | 2020-08-13 | 2020-09-10 |  |  |  |  | New Customer Connection – An existing 12.5 kV customer requested 34.5 kV service, anticipated load is 1 MW with behind the meter generation (2.5 MW), location is near the Windsor – New Canton 34.5 kV line.
EKPC-2020-001 | EKPC | PJM West | 2020-01-17 | 2/21/2020 5/22/2020 | 2020-09-15 | s2287 |  | Marion Co New Customer Load | A new industrial customer has requested a new delivery point for a peak demand of 36 MW by 10/1/2020. The new delivery point is located in Marion Co, KY approximately 0.3 miles from EKPC’s 161 KV transmission near the existing EKPC owned 161/24.9 KV Marion County Industrial Park distribution substation. The existing distribution infrastructure is not capable of serving this request. After additional DNH study by PJM, The Marion Co – Marion IP tap 161kV line is overloaded in the N-1-1 study (The line loading is still 110% of Normal Rating, 84MVA, after system adjustments after loss of Green Co – Summer Shade 161kV line). Currently the Marion Co-Marion Co Industrial Tap 161 KV line has a maximum operating temperature of 142F. This line is limited by a distribution line crossing.
EKPC-2020-002 | EKPC | PJM West | 2020-03-19 | 2020-04-20 |  |  |  | Cincinnati/Northern KY Airport Area Customer Service | The distribution cooperative serving the area in the vicinity of the Cincinnati/Northern Kentucky International Airport has requested that EKPC develop a solution to improve service reliability to customers, provide back-feed capability, and add substation transformer capacity for expected load growth in the area. This area is currently served by EKPC’s W.M. Smith distribution substation. The footprint of that substation is compressed, and future expansion is not possible at that location. Additionally, the existing substation is located on the fringe of the load pocket and is not adjacent to the airport, where the growth is expected to occur.
ME-2019-009 | ME | PJM MA | 2019-02-22 |  |  |  |  | Middletown Junction - Swatara Hill - Campbelltown 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-030 | ME | PJM MA | 2019-07-11 |  |  |  |  | New Customer on the Martins Creek - Siegfried #2 230 kV line | New Customer Connection – A customer requested 230 kV service; anticipated load of approximately 27 MVA; location is near the PPL Martins Creek – Siegfried #2 230 kV line. Requested in-service date is 6/1/2021
ME-2019-031 | ME | PJM MA | 2019-05-31 | [5 empty] | * The loss of Gitts Run substation results in loss of approximately 40 MW of load and approximately 2900 customers. * Substation consists of: * Four 115 kV transmission lines * Two distribution transformers connected to transmission with switches * One normally open bus tie switch
ME-2019-033 | ME | PJM MA | 2019-05-31 | [5 empty] | * The loss of Hamilton substation results in loss of approximately 30 MW of load and approximately 3600 customers. * Substation consists of: * Two 115 kV lines. * Two distribution transformers connected with switches * One generator connected with a switch
ME-2019-034 | ME | PJM MA | 2019-05-31 | [5 empty] | * The loss of Campbelltown substation results in loss of approximately 40 MW of load and approximately 8800 customers. * Substation consists of: * Three networked 69 kV transmission lines * Two distribution transformers connected to bus with switches * No bus tie breaker
ME-2019-039 | ME | PJM MA | 2019-07-31 | 2019-11-18 | 2020-03-20 | s2170 |  | Campbelltown - Middletown - North Hershey 69 kV Line Rebuild | Campbelltown – Middletown – North Hershey 69 kV line sections are exhibiting deterioration. * Total line distance is approximately 19.7 miles. * 260 out of 407 structures failed inspection (64% failure rate). * Failure reasons include age, decay, woodpecker holes. * Transmission line ratings are limited by terminal equipment: * Campbelltown – Campbelltown Tap 69 kV line (substation conductor, disconnect switches, relaying) * Existing line rating: 71/91 MVA (SN/SE) * Existing conductor rating: 139/169 MVA (SN/SE) * Middletown – Wood St Tap 69 kV line (disconnect switches, line relaying, substation conductor) * Existing line rating: 82/103 MVA (SN/SE) * Existing conductor rating: 139/169 MVA (SN/SE)
ME-2019-040 | ME | PJM MA | 2019-07-31 | 2020-07-16 | 2020-10-16 | s2310 |  | Carsonia - Lyons - North Boyertown 69 kV line | Carsonia – Lyons – North Boyertown 69 kV line is exhibiting deterioration. * Total line distance is approximately 22.8 miles. * 339 out of 447 structures failed inspection (76% failure rate). * Failure reasons include age, woodpecker holes, bayonet pole, top rot. Thermal loading on the Clousers Crossing – North Boyertown 69 kV section is ~105% of the SE rating for the N-1-1 loss of the East Topton – Huffs Church 69 kV line section (bus 204829 to bus 20867) & North Boyertown 230-69 kV transformer (ME-P1-2-230- 003) (2018 RTEP Model – 2023 Summer) Transmission line ratings are limited by terminal equipment Lyons – Lyons tap 69 kV line (line relaying) * Existing line rating: 167/167 MVA (SN/SE) * Existing conductor rating: 218/251 MVA (SN/SE)
ME-2019-041 | ME | PJM MA | 2019-07-31 | 2020-07-16 | 2020-10-16 | s2311 |  | Lucent - Muhlenberg 69 kV line | Lucent – Muhlenberg 69 kV line – Terminal equipment has an increased risk of failure (circuit breaker, disconnect switches, line relaying) due to obsolescence of equipment. Limited spare parts are available. * Circuit breakers are 50+ years old with Type U bushings and have a history of oil leaks * Lucent disconnect switch has bad contacts * Line relays have a history of overtripping Transmission line rating is limited by terminal equipment: Lucent – Spring Valley 69 kV line (substation conductor, disconnect switches) * Existing line rating: 71/91 MVA (SN/SE) * Existing conductor rating: 111/134 MVA (SN/SE) Spring Valley – MG Tap 69 kV line (substation conductor, disconnect switches) * Existing line rating: 82/103 MVA (SN/SE) * Existing conductor rating: 111/134 MVA (SN/SE) MG Tap – Muhlenberg 69 kV line (substation conductor, disconnect switches) * Existing line rating: 71/91 MVA (SN/SE) * Existing conductor rating: 111/134 MVA (SN/SE)
ME-2019-042 | ME | PJM MA | 2019-07-31 | 2019-11-18 | 2020-03-20 | s2171 |  | Middletown Junction - Olmsted - Middletown 69 kV Line Terminal Upgrades | Middletown Junction – Olmstead - Middletown 69 kV line – Terminal equipment has an increased risk of failure (circuit breaker, disconnect switches, line relaying) due to obsolescence of equipment. Limited spare parts are available. * Circuit breakers are 50+ years old with Type U bushings * Circuit breakers have a history of failed compressor belt * Circuit breaker has failing dielectric strength Transmission line rating is limited by terminal equipment: Middletown Junction – Olmstead 69 kV line (line relaying) * Existing line rating: 71/91 MVA (SN/SE) * Existing conductor rating: 111/134 MVA (SN/SE) Wood Street Tap – Wood Street 69 kV line (substation conductor) * Existing line rating: 38/49 MVA (SN/SE) * Existing conductor rating: 53/64 (SN/SE) Wood Street Tap – Middletown 69 kV line (substation conductor, disconnect switches, relaying) * Existing line rating: 51/66 MVA (SN/SE) * Existing conductor rating: 139/169 MVA (SN/SE)
ME-2019-043 | ME | PJM MA | 2019-07-31 |  |  |  |  | Carpenter Technology - South Reading 69 kV line | Carpenter Technology – South Reading 69 kV line is exhibiting deterioration. * Total line distance is approximately 5.9 miles. * 125 out of 151 structures failed inspection (83% failure rate). * Failure reasons include age, woodpecker holes, and sound. Transmission line ratings are limited by terminal equipment Carpenter Technology – Glenside 69 kV line (disconnect switches) * Existing line rating: 82/103 MVA (SN/SE) * Existing conductor rating: 102/124 MVA (SN/SE) Glenside – South Reading 69 kV line (disconnect switches, substation conductor) * Existing line rating: 82/103 MVA (SN/SE) * Existing conductor rating: 102/124 MVA (SN/SE)
ME-2019-044 | ME | PJM MA | 2019-07-31 |  |  |  |  | North Boyertown - West Boyertown 69 kV line | North Boyertown – West Boyertown 69 kV line is exhibiting deterioration. * Total line distance is approximately 3.6 miles. * 42 out of 71 structures failed inspection (59% failure rate). * Failure reasons include age, sound, and bayonet pole. Thermal loading on the North Boyertown – West Boyertown 69 kV line is ~88% of the SE rating for loss of the North Boyertown – Cabot 69 kV line section (bus 204606 to bus 204834). (2018 RTEP Model – 2023 Summer) Transmission line ratings are limited by terminal equipment: (substation conductor, line relaying) * Existing line rating: 71/72 MVA (SN/SE) * Existing conductor rating: 80/96 MVA (SN/SE)
ME-2019-045 | ME | PJM MA | 2019-07-31 | 2019-11-18 | 2020-03-20 | s2172 |  | Baldy - East Topton 69 kV Line Terminal Upgrade | Baldy – East Topton 69 kV line – Terminal equipment has an increased risk of failure (circuit breaker and line relaying) due to obsolescence of equipment. Limited spare parts are available. * East Topton circuit breaker is 40+ years old with Type U bushings and has a history of failed oil dielectric strength Transmission line rating is limited by terminal equipment: Baldy – Kutztown 69 kV line (substation conductor) * Existing line rating: 76/90 MVA (SN/SE) * Existing conductor rating: 80/96 MVA (SN/SE) Kutztown – East Topton 69 kV line (substation conductor, line relaying) * Existing line rating: 62/62 MVA (SN/SE) * Existing conductor rating: 80/96 MVA (SN/SE)
ME-2019-046 | ME | PJM MA | 2019-07-31 | 2019-11-18 | 2020-03-20 | s2173 |  | Hamilton – Hunterstown 115 kV Line | Hamilton – Hunterstown 115 kV Line 221/263 232/282 Substation Conductor
ME-2019-047 | ME | PJM MA | 2019-07-31 | 2021-01-14 |  |  |  | North Hanover – Gitts Tap 115 kV Line, Gitts Tap – Fairview 115 kV Line Relays and communication equipment | North Hanover – Gitts Tap 115 kV Line, 221/263, 232/282, Substation Conductor; Gitts Tap – Fairview 115 kV Line, 232/282, 232/282, -
ME-2019-048 | ME | PJM MA | 2019-07-31 | 2021-01-14 |  |  |  | Jackson – Menges Mills 115 kV Line, Menges Mills – PH Glatfelter 115 kV Line Relays and communication equipment | Jackson – Menges Mills 115 kV Line, 163/185, 184/223, Line Trap; Menges Mills – PH Glatfelter 115 kV Line, 221/263, 232/282, Substation Conductor
ME-2019-049 | ME | PJM MA | 2019-07-31 |  |  |  |  | North Hanover – Gitts Run 115 kV Line, Gitts Run – PH Glatfelter 115 kV Line Relays and communication equipment | North Hanover – Gitts Run 115 kV Line, 232/282, 232/282, -; Gitts Run – PH Glatfelter 115 kV Line, 221/263, 232/282, Substation Conductor
ME-2019-050 | ME | PJM MA | 2019-07-31 | 2019-11-18 | 2020-03-20 | s2174 |  | Caterpillar Tractor – Whiteford, Whiteford – Glades 115 kV Lines | Caterpillar Tractor – Whiteford 115 kV Line, 232/277, 232/282, Line Trap; Whiteford – Glades 115 kV Line, 184/223, 184/223, -
ME-2019-052 | ME | PJM MA | 2019-07-31 | 2019-11-18 | 2020-03-20 | s2175 |  | Violet Hill – Queen Street, Queen Street – Springwood, Springwood – Yoe 115, Yoe – Redfront, & Redfront – Yorkana 115 kV Lines | Violet Hill – Queen Street 115 kV Line, 204/266, 232/282, Substation Conductor Queen Street – Springwood 115 kV Line, 232/282, 232/282, - Springwood – Yoe 115 kV Line, 232/282, 232/282, - Yoe – Redfront 115 kV Line, 184/223, 184/223, - Redfront – Yorkana 115 kV Line, 184/223, 184/223, -
ME-2019-053 | ME | PJM MA | 2019-06-28 |  |  |  |  | Raintree 115 kV substation | New Customer Connection – A customer requested 115 kV service; anticipated load is 28 MVA; location is near the Raintree 115 kV substation
ME-2020-001 | ME | PJM MA | 2020-04-14 | 2020-07-07 | 2020-10-16 | s2301 |  | Portland 230/115 kV #3 Transformer | Portland 230/115 kV #3 Transformer was replaced with a spare transformer as a result of a failure in 2017. The transformer was installed on a temporary pad with temporary oil containment.
ME-2020-003 | ME | PJM MA | 2020-04-14 | 2020-07-07 | 2020-10-16 | s2302 |  | Alburtis substation | Current Alburtis configuration has two 230 kV lines and one 500/230 kV transformer connected to a straight bus. A bus outage or breaker failure would result in the loss of these three elements.
ME-2020-004 | ME | PJM MA | 2020-04-16 |  |  |  |  | North Boyertown – West Boyertown 69 kV line terminal equipment | North Boyertown – West Boyertown 69 kV line – Terminal equipment has an increased risk of failure (line relaying and circuit breaker) due to obsolescence of equipment. Limited spare parts are available
ME-2020-005 | ME | PJM MA | 2020-04-16 | 2020-10-15 |  |  |  | South Hamburg – Leesport – North Temple 69 kV line | New Customer Connection – requested 69 kV service; anticipated load is 17 MVA; location is near the South Hamburg – Leesport – North Temple 69 kV line
ME-2020-006 | ME | PJM MA | 2020-04-16 | 2020-11-18 |  |  |  | Germantown 115 kV substation | New Customer Connection – requested 115 kV service; anticipated load is 12 MVA; location is near the Germantown 115 kV substation
ME-2020-007 | ME | PJM MA | 2020-04-16 | 2020-10-15 |  |  |  | North Hanover 115 kV substation | New Customer Connection – requested 115 kV service; anticipated load is 21 MVA; location is near the North Hanover 115 kV substation
ME-2020-008 | ME | PJM MA | 2020-05-12 | 2020-07-07 | 2020-10-16 | s2303 |  | Jackson #4 230/115 kV Transformer | Jackson #4 230/115 kV Transformer has increased failure probability due to: Transformer is 55 years old, Experiencing nitrogen gas leaks, Deteriorated bushings, Obsolete parts, Deteriorated gaskets and seals
ME-2020-009 | ME | PJM MA | 2020-06-16 | 2020-10-15 |  |  |  |  | The Orrtanna tap – Orrtanna section of the Hunterstown – Lincoln – Orrtanna 115 kV 963 line is exhibiting deterioration. • Total line distance is approximately 9 miles. • 73 out of 74 structures failed inspection (99% failure rate). • Failure reasons include age, top rot, woodpecker holes, and cut and missing grounds.
ME-2020-010 | ME | PJM MA | 2020-08-13 | 2020-10-15 |  |  |  |  | New Customer Connection – A customer requested 69 kV service; anticipated load is 9.5 MVA; location is near the MillardsQuarry 69 kV substation
ME-2020-011 | ME | PJM MA | 2020-08-13 | 2020-10-15 |  |  |  |  | New Customer Connection – A customer requested 69 kV service; anticipated load is 10 MVA; location is near the Leesport 69 kV substation
PE-2019-0007 | PE | PJM MA | 2019-07-31 |  |  |  |  | Delaware County, PA | PECO Distribution Planning has been requested to support additional load growth in the Marcus Hook area of Delaware County PA. Initial 2019 Load: 88 MVA ;Projected 2022 Load: 174 MVA
PE-2020-001 | PE | PJM MA | 2020-03-10 |  |  |  |  | Whitpain[PECO] – Bucksmont[PPL] | 230kV tie line 220-10 (Whitpain[PECO] – Bucksmont[PPL] has obsolete relays It is becoming difficult to service existing electromechanical relays. They are being phased out of the system.
PE-2020-002 | PE | PJM MA | 2020-03-10 |  |  |  |  | Whitpain – Jarrett | 230kV line 220-52 (Whitpain – Jarrett) has obsolete relays It is becoming difficult to service existing electromechanical relays. They are being phased out of the system.
PE-2020-003 | PE | PJM MA | 2020-03-10 | 2020-06-02 | 2020-09-10 | s2778 |  | Emilie #8 230/138kV transformer | Emilie #8 230/138kV auto transformer is in deteriorating condition. Dissolved gas analysis (DGA) results indicate internal issues within the transformer
PE-2020-004 | PE | PJM MA | 2020-07-07 | 2020-10-06 | 2020-11-13 | s2361 |  |  | Heaton 230kV circuit breaker #805 installed in 1968 is in deteriorating condition due to SF6 gas leaks, replacement part availability, and elevated maintenance cost.
PE-2020-005 | PE | PJM MA | 2020-07-07 | 2020-10-06 | 2020-11-13 | s2362 |  |  | Woodbourne 230kV circuit breaker #905 installed in 1968 is in deteriorating condition due to SF6 gas leaks, replacement part availability, and elevated maintenance cost.
PE-2020-006 | PE | PJM MA | 2020-07-16 | 2020-09-10 | 2020-11-13 | s2357 |  |  | Cromby 138kV circuit breaker #270 installed in 1953 is in deteriorating condition due to oil leaks, spare part availability, and elevated maintenance cost.
PE-2020-007 | PE | PJM MA | 2020-11-04 | [5 empty] | Waneeta 230kV circuit breaker #285 installed in 1968 is in deteriorating condition due to SF6 gas leaks, replacement part availability, and elevated maintenance cost.
PE-2020-008 | PE | PJM MA | 2020-11-04 | [5 empty] | Tabor 230kV circuit breaker #905 installed in 1968 is in deteriorating condition due to SF6 gas leaks, replacement part availability, and elevated maintenance cost.
PE-2020-009 | PE | PJM MA | 2020-12-01 | [5 empty] | Grays Ferry 230kV circuit breaker #375 installed in 1970 is in deteriorating condition due to SF6 gas leaks, replacement part availability, and elevated maintenance cost
PE-2020-010 | PE | PJM MA | 2020-12-01 | [5 empty] | Whitpain 500kV circuit breaker #575 installed in 1968 is in deteriorating condition due to SF6 gas leaks, replacement part availability, and elevated maintenance cost.
PE-2020-011 | PE | PJM MA | 2020-12-01 | [5 empty] | Whitpain 500kV circuit breaker #385 installed in 1968 is in deteriorating condition due to SF6 gas leaks, replacement part availability, and elevated maintenance cost.
PE-2020-012 | PE | PJM MA | 2020-12-01 | [5 empty] | PECO substation control house equipment for its Eddystone substation is located inside a legacy generation owned facility.
PE-2020-013 | PE | PJM MA | 2020-12-16 | 2021-01-14 |  |  |  |  | Passyunk 69kV circuit breaker #235 installed in 1968 is in deteriorating condition due to oil leaks, replacement part availability, and elevated maintenance cost.
PE-2020-014 | PE | PJM MA | 2020-12-16 | 2021-01-14 |  |  |  |  | Eddystone 138kV circuit breaker #255 installed in 1968 is in deteriorating condition due to oil leaks, replacement part availability, and elevated maintenance cost.
PEP-2020-001 | PEP | PJM MA | 2020-08-04 | 2020-09-01 | 2020-12-07 | s2356 |  |  | 230kV circuits 23067 & 23087 from Oak Grove to Talbert (~10 miles), constructed in 1968, are exhibiting severe material condition issues: - All structures are currently rusting and are at risk for structural failure - All structures need replacement of insulators, conductor, all hardware, lattice coating, foundation/lattice leg repairs, tower attachment points/vangs - 20% structures need immediate grounding replacement, foundation replacement and lattice/bent member repairs - Tested insulator samples no longer meet mechanical design rating
PN-2019-035 | PN | PJM MA | 2019-07-31 |  |  |  |  | Piney – Haynie – Grandview – Titusville – Union City – Erie South 115 kV line | The Piney – Haynie – Grandview – Titusville – Union City – Erie South 115 kV line is exhibiting deterioration. Total line distance is approximately 82.3 miles. 556 out of 697 structures failed inspection (80% failure rate). Failure reasons include age, woodpecker damage, top rot, phase raised, failed sound test, and weatherization. Transmission line ratings are limited by terminal equipment. Piney – Haynie 115 kV line (substation conductor, line relaying, line trap) * Existing line rating: 147/190 MVA (SN/SE) * Existing conductor rating: 202/245 MVA (SN/SE) Haynie – Grandview 115 kV line (substation conductor, line relaying, line trap) * Existing line rating: 147/190 MVA (SN/SE) * Existing conductor rating: 202/245 MVA (SN/SE) Union City – Erie South 115 kV line (substation conductor, line relaying) * Existing line rating: 176/224 MVA (SN/SE) * Existing conductor rating: 232/282 MVA (SN/SE)
PN-2019-036 | PN | PJM MA | 2019-10-21 |  |  |  |  | Eagle Valley – Westfall 115 kV line Rehab | The Eagle Valley – Westfall 115 kV line is exhibiting deterioration resulting in increased maintenance. The structures are approaching end of life. The line was originally constructed in 1956. * Total line distance is approximately 20.7 miles * 147 out of 154 structures failed inspection (95% failure rate) * Failure reasons include age, woodpecker damage, cracking, and decay.
PN-2019-037 | PN | PJM MA | 2019-10-21 | 2019-11-18 | 2020-03-20 | s2176 |  | Seward –Tower 51 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ PN-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ 037 ¦ Seward –Tower 51 115 kV Line ¦ 147/185 ¦ 201/244 ¦ Circuit Breaker, Line Relaying, Line Trap, Substation Conductor ¦
PN-2020-001 | PN | PJM MA | 2020-05-12 | 2020-07-07 | 2020-10-16 | s2304 |  | Hooversville #3 230/115 kV Transformer | Hooversville #3 230/115 kV Transformer has increased failure probability due to: Transformer is 43 years old, Type “U” bushings, High level heating gases and moisture , Obsolete parts, Nitrogen and oil leaks
PN-2020-002 | PN | PJM MA | 2020-05-12 | 2020-07-07 | 2020-10-16 | s2305 |  | Erie West #1 345/115 kV Transformer | Erie West #1 345/115 kV Transformer has increased failure probability due to: Transformer is 47 years old, High level heating gases and moisture, HV bushings have, significant deterioration, Obsolete parts, Nitrogen and oil leaks
PN-2020-003 | PN | PJM MA | 2020-04-14 | 2020-06-02 | 2020-09-22 | s2279 |  | Shelocta 230 kV bus | The Shelocta 230 kV bus is a three terminal line consisting of two 230 kV lines and a 230/115 kV transformer. An N-1 outage results in the loss of all three networked elements
PN-2020-004 | PN | PJM MA | 2020-04-16 | [5 empty] | Transmission line ratings are limited by terminal equipment:Grandview –Haynie 115 kV Line,Haynie –Piney 115 kV Line,Burma –Piney 115 kV Line,Eclipse –Piney 115kV Line; Multiple System Condition Issues Identified at Piney 115 kV Substation and Grandview 115 kV Substation
PN-2020-005 | PN | PJM MA | 2020-05-12 | [5 empty] | Erie South – Erie West 345 kV Line: Relay schemes that have a history of misoperation, Obsolete and difficult to repair communication equipment (DTT, Blocking, etc.),
PN-2020-007 | PN | PJM MA | 2020-05-12 | 2020-07-07 | 2020-10-16 | s2306 |  | Altoona #1 230-46 kV Transformer | Altoona #1 230-46 kV Transformer has increased failure probability due to: Transformer is 55 years old, Poor oil quality in LTC, Nitrogen leaks in tank, Bushing H3 oil leaks
PN-2020-008 | PN | PJM MA | 2020-05-12 | 2020-07-07 | 2020-10-16 | s2307 |  | Altoona #2 230-46 kV Transformer | Altoona #2 230-46 kV Transformer has increased failure probability due to: Transformer is 47 years old, Nitrogen leaks in tank, LTC oil leak, Pump flanges are leaking, SCADA alarms are not functional
PN-2020-009 | PN | PJM MA | 2020-05-21 |  |  |  |  | Somerset – Ralphton - Hooversville 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. • Proper operation of the protection scheme requires all the separate components perform adequately during a fault. • In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. • Transmission line ratings are limited by terminal equipment.
PN-2020-010 | PN | PJM MA | 2020-05-21 | 2020-07-16 | 2020-10-16 | s2312 |  | Hooversville - Tower 51 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. • Proper operation of the protection scheme requires all the separate components perform adequately during a fault. • In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. • Transmission line ratings are limited by terminal equipment.
PN-2020-011 | PN | PJM MA | 2020-05-21 | 2020-11-18 |  |  |  | Erie South – GESG Tap - Gore Junction & Green Garden 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. • Proper operation of the protection scheme requires all the separate components perform adequately during a fault. • In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. • Transmission line ratings are limited by terminal equipment.
PN-2020-012 | PN | PJM MA | 2020-05-21 | 2020-07-16 | 2020-10-16 | s2313 |  | Morgan Street – Franklin Tap - Air Products – Geneva 115 kV | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. • Proper operation of the protection scheme requires all the separate components perform adequately during a fault. • In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. • Transmission line ratings are limited by terminal equipment.
PN-2020-013 | PN | PJM MA | 2020-08-13 | [5 empty] | The Reeds Switching Station – Reeds Gap – Blain 115 kV line was originally constructed in 1967 and is exhibiting deterioration. • Total line distance is approximately 9.8 miles • 72 out of 77 wood structures failed inspection (93% failure rate) • Failure reasons include rotten/cracked poles, decay, top rot, woodpecker, and cracked arms and braces Transmission line ratings are limited by terminal equipment. Reeds Switching Station – Reeds Gap 115 kV Line (substation conductor) • Existing line rating: 86 / 99 MVA (SN / SE) • Existing conductor rating: 95 / 99 MVA (SN / SE) Reeds Gap – Blain 115 kV Line (substation conductor) • Existing line rating: 88 / 129 MVA (SN / SE) • Existing conductor rating: 133 / 160 MVA (SN / SE)
PN-2020-014 | PN | PJM MA | 2020-05-21 |  |  |  |  | Raystown – McConnellstown 46 kV | The Raystown– McConnellstown 46 kV line has three in-line switches (A-136, A-137, and A-139) that are in degraded condition and have limited availability of spare parts. The existing switches have operational limitations. The motor control units are no longer supported by the manufacturer. Inability to sectionalize this line results in loss of approximately 9 MW of load and approximately 1,136 customers, including a REA. Transmission line ratings are limited by terminal equipment. • Allegheny Hydro Tap – Allegheny Hydro 46 kV line rating is limited by the transmission line conductor 52 / 62 MVA (SN/SE). • Allegheny Hydro Tap – RAM Junction 46 kV line rating is 55 / 69 MVA (SN/SE) and the transmission line conductor rating is 59 / 71 MVA (SN/SE). (disconnect switch) • RAM Junction – Piney Ridge 46 kV line rating is 55 / 69 MVA (SN/SE) and the transmission line conductor rating is 59 / 71 MVA (SN/SE). (disconnect switch)
PN-2020-015 | PN | PJM MA | 2020-05-21 | 2020-07-16 | 2020-10-16 | s2314.1 |  | Blairsville East – Social Hall 138 kV | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. • Proper operation of the protection scheme requires all the separate components perform adequately during a fault. • In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. • Transmission line ratings are limited by terminal equipment.
PN-2020-016 | PN | PJM MA | 2020-07-16 | [5 empty] | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. • Proper operation of the protection scheme requires all the separate components perform adequately during a fault. • In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. • Transmission line ratings are limited by terminal equipment.
PN-2020-017 | PN | PJM MA | 2020-08-13 | 2020-11-18 |  |  |  |  | The loss of Nanty Glo substation results in loss of approximately 6.6 MW of load and approximately 1,600 customers. Substation consists of: • Four networked 46 kV lines • Two distribution transformers connected with switches Transmission line ratings are limited by terminal equipment. Nanty Glo – Revloc46 kV Line (line relaying, substation conductor) • Existing line rating: 26 / 26 MVA (SN / SE) • Existing conductor rating: 37 / 37 MVA (SN / SE) Nanty Glo – Beth Colleries S 46 kV Line (line relaying) • Existing line rating: 25 / 25 MVA (SN / SE) • Existing conductor rating: 32 / 32 MVA (SN / SE) Beth Colleries – Jackson Road S 46 kV Line (line relaying, substation conductor) • Existing line rating: 33 / 33 MVA (SN / SE) • Existing conductor rating: 49 / 50 MVA (SN / SE)
PN-2021-001 | PN | PJM MA | 2021-01-14 | 2021-02-16 |  |  |  |  | The Chestnut Flats and Sandy Ridge 115 kV wind generators can island with 34.5 kV load at Philipsburg, and 46 kV load at Tyrone North and Westfall under certain N-1-1 conditions. Transmission line ratings are limited by terminal equipment. Philipsburg – Shawville 115 kV Line (line trap, circuit breaker) • Existing line rating: 163 / 185 MVA (SN / SE) • Existing conductor rating: 167 / 202 MVA (SN / SE)
PPL-2019-0019 | PPL | PJM MA | 2019-12-16 | 2020-02-11 | 2020-06-02 | s2202 |  | West Allentown, PA | New customer has submitted a request to have their facility served from a 69 kV transmission line. The load is approximately 25 MVA.
PPL-2019-0020 | PPL | PJM MA | 2019-12-16 | 2020-02-11 | 2020-06-02 | s2203 |  | West Allentown, PA | New customer has submitted a request to have their facility served from a 69 kV transmission line. The load is approximately 12 MVA.
PPL-2019-0021 | PPL | PJM MA | 2019-12-16 | 2020-02-11 | 2020-06-02 | s2204 |  | Harrisburg, PA | New customer has submitted a request to have their facility served from a 69 kV transmission line. The load is approximately 5 MVA.
PPL-2019-003 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Beavertown 69kV Tap line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets that were installed in 1962.
PPL-2019-004 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Hauto-Frackville #1 69kV line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets installed in 1923.
PPL-2019-006 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Lycoming 2-Muncy Tie 69kV line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets installed in 1954
PPL-2019-007 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Lycoming-Williamsport 1&2 and South Williamsport Tap 1&2 69kV line is a reliability risk due to aging infrastructure and poor asset health. The line is in poor condition with the majority of the original assets installed in 1930.
PPL-2019-015 | PPL | PJM MA | 2019-02-22 | 2019-11-18 | 2020-06-02 | s2168 |  | Ringtown 69 kV Tap | PPL Distribution has submitted a request for a 69 kV transmission source to their new Epsilon 69/12kV substation.
DOM-2021-0014 | DOM | PJM South | 2021-03-09 | [5 empty] | Dominion Energy has identified a need to replace 79 existing transmission towers that carry 230 kV Line #272 (Dooms - Grottoes). The need for replacement is based on the Company’s End of Life criteria. The 11.5-mile-long line consists of CORTEN X-Series lattice-type towers that were constructed in 1967. These towers have inherent corrosion problems causing continuous deterioration to the steel members and have reached the end of their useful life. They are amongst the weakest and most problematic CORTEN lattice towers on our system and are a high priority for replacement.
DOM-2021-0016 | DOM | PJM South | 2021-03-09 | [5 empty] | DEV Distribution has submitted a DP Request for a new substation (Interconnection) to accommodate a new datacenter campus in Loudoun County with a total load in excess of 100MW. Requested in-service date is 12/15/2024.
Dayton-2021-001 | Dayton | PJM West | 2021-02-17 |  |  |  |  | Preble County, Ohio | •DP&L Distribution has requested a new 69kV or 138kV delivery point to replace the existing New Westville 33kV Substation due to poor performance and lack of standard equipment which could lead to prolonged system outages.
DEOK 2020-006 | DEOK 2020 | PJM West | 2021-02-17 |  |  |  |  | Summerside | The 34 kV bus at Summerside is fed by two transformers. TB2 is a 138/69/34 kV transformer with breaker connections on the 138 and 69 kV buses. The 34kV winding feeds through a voltage regulator then and a switch breaker connection to the 34 kV bus. TB5 is a 138/34 kV transformer with switch breaker connections to the 138 and 34 kV buses. This arrangement exposes the transmission system to faults from the 34 kV system. This arrangement exposes TB2 to faults from the distribution system.
DEOK 2021-001 | DEOK 2021 | PJM West | 2021-02-17 |  |  |  |  | Seward | An existing customer has requested an additional 20MW of distribution service by summer of 2022. This exceeds the capability of the existing distribution infrastructure in the local area. Duke Energy Distribution has requested additional capacity delivery through Seward substation.
AEP-2021-IM001 | AEP | PJM West | 2021-02-17 |  |  |  |  | South Bend - New Carlisle 138kV | 0.88 miles of double circuit 1930 steel lattice line/ Original 397 MCM ACSR and steel structures are still on the line/There is one structure with open conditions ( 20% of line) relating to worn shield wire hardware/ Circuit 1 has had 3 momentary outages and 3 permanent outages since 2016/ Cicruit 2 had 1 permenant outage since 2015/ Circuit is a tie with NIPSCO
AEP-2021-IM002 | AEP | PJM West | 2021-02-17 |  |  |  |  | New Carlisle – Maple 138kV | 0.86 miles of 1952 wood pole H frame line/Utilizes original structures and 397 ACSR from 1952/5 structures have open conditions (63% of line) relating to pole rot, split or rot crossarms, broken ground lead wire, rusty guy wires, and cracked static bracket/2 momentary outages over the past 5 years/Circuit is an interconnection with NIPSCO and MISO
AEP-2020-IM004 | AEP | PJM West | 2021-02-17 |  |  |  |  | Spy Run Transformer | •Manufactured in 1975/Per DGA analysis, this transformer has increased levels of gassing of Ethylene, Ethane, and CO2/The low level of dielectric strength indicates acid coating insulation with sludge ready to deposit in the transformer, increasing the risk of failure./The levels of moisture and dielectric strength indicate the insulation system is in poor condition, reducing the ability of the unit to withstand through faults.
AEP-2021-IM006 | AEP | PJM West | 2021-02-17 |  |  |  |  | Wolf Lake 69kV Tap | Wolf Lake Tap 69kV ~5.44 Miles/Original Construction Date: 1958/Original Construction Type: Wood pole with 4/0 ACSR conductor (57/68 structures original from 1958) Outage History (2015-2020)/697,305/CMI with 8 momentary and 1 permanent outages/Radial service to Wolf Lake. Radial service severely restricts the ability to perform routine maintenance and restoration activities, which can degrade the reliability of the associated lines/equipment in comparison to other non-radial facilities. Additional Info:12 of 30 structures assessed by ground crew/UAV showed some level of wood pole decay/Structures do not meet 2017 NESC Grade B loading criteria, do not meet current AEP structural strength requirements, and do not meet the current ASCE structural strength requirements.
AEP-2021-IM011 | AEP | PJM West | 2021-02-17 |  |  |  |  | Lincoln 138/69/34.5kV | Lincoln 138/69/34.5kV CB “B”, “C” and “I” are 1995, 1988 and 1987 vintage 145-PA type breakers The 145-PA Type Breakers are experiencing marked increases in malfunctions. There have been 437 recorded malfunctions on 132 total units of this model type on the AEP System. The most common issues are related to loss of SF6 gas and mis-operations. The expected life of the bushing gaskets and door inspection port seals is 25 years; all three of these units have reached this age. Seals that are no longer adequate can cause SF6 leaks to become more frequent. Low SF6 pressure in the breaker reduces the ability of the breaker to correctly interrupt a fault. Additionally, low pressure alarms and SF6 leaks lead to increased maintenance costs. The manufacturer provides no support or parts for this model of circuit breakers. Finally, SF6 leaks impact the environment. CB “B” has experienced 37 fault operations
AEP-2021-IM012 | AEP | PJM West | 2021-02-17 |  |  |  |  | Decker 69kV Load Addition | City of Bluffton has requested an expansion to their delivery point at Decker 69 kV station to serve a new 15.8MW load by November 1 2021.
AEP-2021-OH003 | AEP | PJM West | 2021-02-17 |  |  |  |  | Hancock, Ohio | Buckeye is requesting on behalf of Hancock-Wood Electric Co-op a new 138kV delivery point on the Ebersole – Findlay Center 138kV Circuit by August 2023. Anticipated load is about 3 MVA.
AEP-2021-OH004 | AEP | PJM West | 2021-02-17 |  |  |  |  | Mark Center SW | Mark Center Switch 69kV: Circuit Breakers B, C, & D: Breaker Age: B 1956, C 1967, & D 1975 Interrupting Medium: (Oil) Fault Operations: Number of Fault Operations: B 26 , C 140, & D 40 Additional Breaker Information: The breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling. Oil spills are common and can result in significant environmental mitigation costs. Relays: Currently, 41 of the 47 relays (87% of all station relays) are in need of replacement. 39 of these are of the electromechanical type and 2 of these are of the static type which have significant limitations with regards to spare part availability, SCADA functionality, and fault data collection and retention.
AEP-2021-OH005 | AEP | PJM West | 2021-02-17 |  |  |  |  | Fairfield County, OH | A customer has requested transmission service near AEP’s existing Bixby – West Lancaster 138 kV circuit in Lancaster, OH. The customer has indicated an initial peak demand of 100 MW with the potential for an ultimate capacity of up to 300 MW at the site.
AEP-2021-OH006 | AEP | PJM West | 2021-02-17 |  |  |  |  | Guernesy County, Ohio | Line Name: Newcomerstown- Cambridge 69kV, Leatherwood- North Cambridge 69kV Original Install Date (Age): 1926 Length of Line: 21.94 miles Total structure count: 317 Original Line Construction Type: Steel lattice and Wood 3% of structures recently replaced Conductor Type: 3/0 Copper 7 and 336 ACSR 18/1 conductor Outage History 18 momentary and 5 permanent outages with an average duration of 33.41 hours CMI: 453,409 from 1/1/2014 – 3/20/2019 Load at Risk: 16.829 MVA Condition Summary Number of open conditions by type / defects / inspection failures: Newcomerstown- Cambridge 88, Leatherwood- North Cambridge 13 Ground lead wire missing, stolen or broken, structure related conditions affecting the cross arm or pole including rot, split or woodpecker holes, contaminated or broken insulator hardware
AEP-2021-OH007 | AEP | PJM West | 2021-02-17 |  |  |  |  | Fremont, Ohio | Fremont Center Station: 69 kV Circuit Breakers F, G, H, J, K, & L Breaker Age: F-1971, G-1971, H-1971, J-1971, K-1971, & L-1988 Interrupting Medium: (Oil) Fault Operations: Number of Fault Operations: F-15, G-51, H-26, J-20, K-19, & L-69 Manufacturer recommended Number of Operations: 10 Additional Breaker Information: These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. Relays: Currently, 40 of the 76 relays (53% of all station relays) are in need of replacement or upgrades. 39 of these are of the electromechanical type and 1 of the static type which have significant limitations with regards to fault data collection, SCADA functionality, spare parts, and data retention. RTU: The existing Data Concentrator – DOS type RTU installed at Fremont Center is a non-standard RTU with no vendor support, no active warranty, and no Ethernet compatibility. In addition, this unit has high a malfunction rate.
AEP-2021-OH008 | AEP | PJM West | 2021-02-17 |  |  |  |  | Lima, Ohio | Circuit Breakers (34.5 kV): F, G, H, I, J, L, M, N, U, V, & W Breaker Age: F, G, H, I, J, L, N, U, & V (1952); M (1955); W (1951) Transformers: 138/34.5/12 kV Transformer Bank 1 (three single phase units) Age: 1941 (all units) The single phase units of this transformer are showing signs of decomposition of the paper insulation that impairs the unit’s ability to withstand future short circuit or through fault events. The units are also showing signs of increased particle contamination and degraded dielectric strength of the insulation system (oil and paper) No oil containment 138/34.5/12 kV Transformer Bank 2 (three single phase units) Age: 1941 (unit 1); 1949 (units 2&3) The single phase units of this transformer are showing signs of increased particle contamination and degraded dielectric strength of the insulation system (oil and paper) No oil containment 138/34.5/12 kV Transformer Bank 3 Age: 1955 This 3-phase unit is showing signs of decomposition of the paper insulation that impairs the unit’s ability to withstand future short circuit or through fault events. This unit is also showing signs of degradation of dielectric strength of the insulation system (oil and paper). No Oil Containment Relays: Currently, 156 of the 174 relays (90% of all station relays) are in need of replacement. 152 of these are of the electromechanical type and 3 are of the static type which have significant limitations with regards to spare part availability and fault data collection and retention. In addition, these relays have no vendor support. Additional Issues: Ground grid concerns: 1 ground per structure 138kV and 34.5kV bays have cap-and-pin insulators All four Transformers have high-side Motor Operated Air Brake switches (MOABs) that are obsolete. There is insufficient road access to get into the station. Need to cross highly utilized railroad crossing to enter the station. There are no crossing signs or barricades which causes safety concerns. An alternative route into the station is needed. Washout risks on the north side of the station. Environmental concerns with the old oil house and underground pipes that were used to pump oil to the 138kV CBs. There are also leftover oil storage tanks and drums on the site. 34.5kV bus is within reaching distance, which causes safety concerns. 34.5kV line PTs are leaking oil and obsolete. Station configuration: Bus tie switches on 138kV Bus 1 & 2. Station Service: Transformers are obsolete, rusting and cable insulation is cracking and contains PCBs. Interrupting Medium: (Oil) Fault Operations: Number of Fault Operations: F 48, G 1, H 1, I 4, J 2, L 2, M 3, N 21, U 10, V 50, & W 13 These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. Circuit Breakers (138 kV): Circuit Breakers: A, D, E, & C Breaker Age: A, D, E, & C (1986) Interrupting Medium: (SF6) Fault Operations: Number of Fault Operations: A 17, D 2, E 2, & C 1 Additional Information: Breaker models for these are 145-PA. The 145-PA Type Breakers are experiencing marked increases in malfunctions. There have been 437 recorded malfunctions on 132 total units of this model type on the AEP System. The most common issues are related to loss of SF6 gas and mis-operations. The expected life of the bushing gaskets and door inspection port seals is 25 years; all four of these units have reached this age. Seals that are no longer adequate can cause SF6 leaks to become more frequent. Low SF6 pressure in the breaker reduces the ability of the breaker to correctly interrupt a fault. Additionally, low pressure alarms and SF6 leaks lead to increased maintenance costs. The manufacturer provides no support or parts for this model of circuit breakers. Finally, SF6 leaks impact the environment.
EKPC-2021-001 | EKPC | PJM West | 2021-02-17 |  |  |  |  | Boone-Bullittsville 69 KV | The 6.4 mile, Boone-Bullittsville 69 KV transmission line is 60 years old. Testing from the LineVue robot from Kinectrics Corporation deemed the phase and static wire condition as unacceptable. The testing identified instances of rusting, pitting, and broken strands. Based on this testing information, the EKPC Reliability team has concluded that this line should be addressed due to the condition assessment. Also, the current configuration of the transmission lines routed into the Boone County transmission station has created lines crossing at undesirable angles. This produces safety issues and possible longer outage times during maintenance activities.
EKPC-2021-002 | EKPC | PJM West | 2021-02-17 |  |  |  |  | Hodgenville - Magnolia 69kV | The 8.49 mile, Hodgenville-Magnolia 69 KV transmission line is 64 years old. Testing from the LineVue robot from Kinectrics Corporation deemed the phase and static wire condition as unacceptable. The testing identified instances of rusting, pitting, and broken strands. Based on this testing information, the EKPC Reliability team has concluded that this line should be addressed due to the condition assessment.
EKPC-2021-003 | EKPC | PJM West | 2021-02-17 |  |  |  |  | Summersville - Magnolia 69kV | The 15 mile, Summersville-Magnolia 69 KV transmission line is 59 years old. Testing from the LineVue robot from Kinectrics Corporation deemed the phase and static wire condition as unacceptable. The testing identified instances of rusting, pitting, and broken strands. Based on this testing information, the EKPC Reliability team has concluded that this line should be addressed due to the condition assessment.
EKPC-2021-004 | EKPC | PJM West | 2021-02-17 |  |  |  |  | Millers Creek | The Millers Creek substation was built in 1965. It has continued to show up on EKPC’s list of Worst Performing areas for several years, and it is currently the #2 worst performing location. It is served on the LG&E/KU 69 KV transmission line between Beattyville and West Irvine. This substation had 12 transmission related outages for the 2015-2019 period. The substation has multiple issues related to poor site access, degraded condition, safety, and obsolete design. Degradation issues include failing fence and erosion around the perimeter of the substation. There is an atypical metering structure with no bypass capability making maintenance more difficult. Regulators are under the low bay structure and are difficult to remove in the event of a failure. Regulator bypass switches and energized feeders have spacing and clearance issues and there is no bypass bus.
EKPC-2021-005 | EKPC | PJM West | 2021-02-17 |  |  |  |  | East Bernstadt | Options are being evaluated to address aging condition issues of the East Bernstadt distribution substation. It has been determined that more space is needed to achieve EKPC’s standard substation design requirements. EKPC’s planning department has been asked to evaluate the ongoing need of the East Bernstadt 16.2 MVAR capacitor bank due to space limitations at the site.
EKPC-2021-006 | EKPC | PJM West | 2021-02-17 |  |  |  |  | Lees Lick | Options are being evaluated to address aging condition issues of the Lees Lick distribution substation. It has been determined that more space is needed to achieve EKPC’s standard substation design requirements. EKPC’s planning department has been asked to evaluate the ongoing need of the Lees Lick 10.72 MVAR capacitor bank due to space limitations at the site.
NEET-2021-01 | NEET | PJM West | 2021-02-17 |  |  |  |  | NEET MA | NEET MidAtlantic IN 345kV (double-circuit) transmission line assets are ~20 miles representing four segments. Asset represents 115 galvanized steel lattice structures: Transmission lines were built in 1958 and are over 60 years old. Reliability concerns with increased failure probability is expected as components have exceeded the industry recommended service life The existing 1414 kCMIL (62/19) paper expanded conductor is obsolete and no longer manufactured Structural components are exhibiting significant deterioration Structural corrosion, insulator EOL, foundation wear, lack of cathodic protection, missing structural components and section loss, etc.
AEP-2020-AEP001 | AEP | PJM West | 2020-12-01 |  |  |  |  | Ratings Methodology Changes | AEP is proposing to implement a ratings methodology change whereby single element open ratings would be applied to all facilities as part of their overall rating. This is to avoid any compliance violations of FAC-008 and TOP standards in case a breaker is opened. AEP’s historic practice was to apply a 2x multiplier to any facilities that connected in a configuration where flow could split between two paths in a station. This practice has been eliminated for any new facilities being constructed. AEP has maintained a list of facilities that continue to operate with a 2x multiplier on them pending future analysis and/or projects to address them For the 2025 RTEP analysis, AEP worked with PJM to apply single multiplier ratings to all facilities on the system There were four lines that were flagged in the 2025 analysis that show potential violations Muskingum-Waterford 345 kV line Jefferson-Clifty Creek 345 kV line East Lima 345/138 kV transformer Olive-New Carlisle 138 kV line (flagged in market efficiency analysis) AEP is proposing to address these needs in order to eliminate the exceptions and apply all single element open ratings in our future cases and in real time operations to comply with the request from PJM Operations and Planning
AEP-2020-AP047 | AEP | PJM West | 2020-12-18 |  |  |  |  | Perry County, KY | Hazard – Bonnyman 69kV #1 Original Install Date (Age): 1940 Length of Line: 9.5 mi Total structure count: 49 Original Line Construction Type: Wood Conductor Type: 336,400 ACSR Momentary/Permanent Outages and Duration: 10 Momentary and 3 permanent Outage CMI (last 5 years only): 185,875 minutes Line Conditions 22 structures with at least one open condition, 45% of the structures on this circuit. 45 structure related open conditions: crossarms and poles including rot, damaged, insect damaged, woodpecker hole, burnt, and bowed conditions. 3 shield wire conditions with damaged and broken strands. 1 broken ground wire lead 2 broken insulators
AEP-2020-OH046 | AEP | PJM West | 2020-11-20 |  |  |  |  | Allen County, Ohio | Station/Area Name: Bluelick Switch 34.5 kV Load: 3.185MW Existing/3.7MW projected by 2029 Customer Request: The customer has requested to upgrade their existing delivery point from 34.5 kV to 69 kV. Requested In-service Date: 6/1/2024
AEP-2020-OH048 | AEP | PJM West | 2020-12-18 |  |  |  |  | Licking County, OH | A customer has requested transmission service at a site just south of the existing Conesville – Corridor 345 kV circuit in New Albany, OH. The customer has indicated an initial peak demand of 64 MW with an ultimate capacity of up to 256 MW at the site.
AEP-2020-OH049 | AEP | PJM West | 2020-12-18 |  |  |  |  | Pickaway County Area, Ohio | Westfall Delivery Point (SCP) 138kV: Buckeye Power Inc., on behalf of South Central Power Company, has requested transmission service in Wayne Township, Pickaway County, Ohio. SCP currently has a radial 69 kV line served out of AEP’s West Lancaster Station with a load of approximately 42.5 MW in 2022 and growth at a rate of 2% per year. South Central Power Company would like a new transmission delivery point on the on the other end of this long 69 kV radial line (44 miles of exposure; 5 delivery points). Service is requested by March 2022.
PPL-2019-018 | PPL | PJM MA | 2019-02-22 | 2019-11-18 | 2020-06-02 | s2169 |  | Theta 69 kV Tap | PPL Distribution has submitted a request for a 69 kV transmission source to their new Theta 69/12kV substation
PPL-2020-0001 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2363 |  |  | Over a 5 mile stretch of the Summit-Lackawanna 1 & 2 230kV line, there are 30 weathering steel Corten lattice towers that were installed in 1970. • 62% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. There will be several thermal violations and approximately175 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0002 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2364 |  |  | Over a 4.1 mile stretch of the Elimsport-Lycoming 2 & 3 230kV line, there are 25 weathering steel Corten lattice towers that were installed in 1971. • 76% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. Approximately 315 MW of local load will be out of power for the next N1 contingency without this circuit.
PPL-2020-0003 | PPL | PJM MA | 2020-09-01 | 2020-10-15 | 2020-11-04 | s2365 |  | Manor-Millwood 230kV & Face Rock-Millwood 1 69kV | Over a 5.2 mile stretch of the Manor-Millwood 230kV line and Face Rock-Millwood 1 69kV line, there are 28 weathering steel Corten lattice towers that were installed in 1967. • 83% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve approximately 200 MW of local load. Absence of this line will cause a thermal violation for the next N-1 contingency.
PPL-2020-0004 | PPL | PJM MA | 2020-09-01 | 2020-10-06 |  |  |  |  | Over a 10.7 mile stretch of the Montour-Milton 230kV line, there are 63 weathering steel Corten lattice towers that were installed in 1971. • 72% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. There will be several thermal violations and approximately 105 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0005 | PPL | PJM MA | 2020-09-01 | 2020-10-15 | 2020-11-04 | s2366 |  | Sunbury-Milton 230kV & Sunbury-Milton 69kV | Over a 10.4 mile stretch of the Sunbury-Milton 230kV and SunburyMilton 69kV lines, there are 68 weathering steel Corten lattice towers that were installed in 1969. • 99% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. There will be several thermal violations and approximately 105 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0006 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2367 |  |  | Over a 7.7 mile stretch of the Stanton-Summit 3 & 4 230kV lines, there are 46 weathering steel Corten lattice towers that were installed in 1970. • 76% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. There will be thermal and voltage violations and approximately 175 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0007 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2368 |  |  | Over an 8.0 mile stretch of the Saegers-Elimsport and ClintonElimsport/Clinton-Saegers 230kV lines, there are 48 weathering steel Corten lattice towers that were installed in 1971. • 69% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. Approximately 465 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0008 | PPL | PJM MA | 2020-09-01 | 2020-10-15 | 2020-11-04 | s2369 |  | South Akron-Millwood 230kV & Millwood-Strasburg tie 69kV | Over a 20.4 mile stretch of the South Akron-Millwood 230kV and the Millwood-Strasburg tie 69kV lines, there are 125 weathering steel Corten lattice towers that were installed in 1967. • 97% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230/69 kV circuit required to serve approximately 25 MW of local load. Absence of this circuit will cause several thermal and voltage violations in the area for the next N-1 contingency.
PPL-2020-0009 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2370 |  |  | Over a 6.2 mile stretch of the Montour-Saegers 1 & 2 230kV lines, there are 38 weathering steel Corten lattice towers that were installed in 1971. • 35% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. Approximately 465 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0010 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2371 |  |  | Over an 8.5 mile stretch of the Jenkins-Stanton and Mountain-Stanton 230kV lines, there are 49 weathering steel Corten lattice towers that were installed in 1972. • 95% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. There will be thermal and voltage violations and approximately 175 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0011 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2372 |  |  | Over a 9.8 mile stretch of the Mountain-Stanton and Mountain-Jenkins 230kV lines, there are 55 weathering steel Corten lattice towers that were installed in 1972. • 97% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. Approximately 190 MW of local load will be out of power for the next N1 contingency without this circuit.
PPL-2020-0012 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2373 |  |  | Over a 21.9 mile stretch of the Montour-Susquehanna and MontourSusquehanna T10 230kV lines, there are 132 weathering steel Corten lattice towers that were installed in 1971. • 74% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. There will be several thermal violations and approximately 60 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0013 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2374 |  |  | Over a 38.0 mile stretch of the Siegfried-Harwood and Harwood-East Palmerton/Siegfried-East Palmerton 230kV lines, there are 221 weathering steel Corten lattice towers that were installed in 1969. • 94% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. There will be a thermal violation and approximately 280 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0014 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2375 |  |  | Over a 9.25 mile stretch of the Montour-Columbia 230kV line, there are 42 weathering steel Corten lattice towers that were installed in 1973. • 86% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. There will be thermal & voltage violations and approximately 400 MW of local load will be out of power for the next N-1 contingency without this circuit.
PPL-2020-0015 | PPL | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-04 | s2376 |  |  | Over a 25.9 mile stretch of the Frackville-Columbia 230kV line, there are 115 weathering steel Corten lattice towers that were installed in 1973. • 93% of the structures on this line are Corten Towers. • A third-party inspection and analysis was conducted on a statistically significant sample of 192 out of the 1284 Corten structures on the PPL system. All the towers inspected exhibited section loss on numerous members and over 90% of the joints had visible pack-out. • The report rated all the Corten towers inspected in poor or worse condition and concluded that the towers require near-term mitigation. • This is an important 230 kV circuit required to serve the local load. Approximately 245 MW of local load will be out of power for the next N1 contingency without this circuit.
PPL-2020-0016 | PPL | PJM MA | 2020-11-18 | 2020-12-16 |  |  |  |  | A new customer has submitted a request to have their facility served from a 69kV transmission line in Dunmore, PA. The load is approximately 15 MVA
PPL-2020-0017 | PPL | PJM MA | 2020-11-18 | 2020-12-16 |  |  |  |  | A new customer has submitted a request to have their facility served from a 69kV transmission line in Hazle Township, PA. The load is approximately 12 MVA
PPL-2020-0018 | PPL | PJM MA | 2020-11-18 | 2020-12-16 |  |  |  |  | A new customer has submitted a request to have their facility served from a 69kV transmission line in McAdoo, PA. The load is approximately 14 MVA
PSEG-2020-0001 | PSEG | PJM MA | 2020-04-14 | 2020-06-02 | 2020-08-31 | s2276 |  | Cinnaminson and Levittown stations | Cinnaminson and Levittown are stations in the Northern Camden/ Southern Burlington area respectively at capacity of 120 MVA each. The stations are currently at capacity. Cinnaminson serves roughly 20,500 customers with peak load of 121 MVA in 2019;Levittown serves roughly 34,000 customers with peak load of 126 MVA in 2019
PSEG-2020-0002 | PSEG | PJM MA | 2020-07-07 | 2020-08-04 | 2020-10-12 | s2316 |  | Western Essex County Area | West Caldwell is a station in the Western Essex County area at capacity of 120 MVA. Marion Drive is a station in the Western Essex County area at capacity of 60 MVA. West Caldwell serves roughly 18,000 customers with peak load of 131 MVA in 2019. Marion Drive serves roughly 18,200 customers with peak load of 62 MVA in 2019.
PSEG-2020-0003 | PSEG | PJM MA | 2020-05-21 | 2020-08-13 | 2020-10-12 | s2317 |  |  | Oak Street is supplied by two 26kV circuits with increasing performance problems. The station is configured with a normally open 26kV bus and normally open 4kV bus. The station is currently not designed for N-1. • Over the past decade, the 26kV supply circuits have seen 14 momentary and 10 extended outages, with total duration of 143 hours. • Station equipment at Oak Street has been in service since 1961 and needs to be addressed. • Oak Street serves roughly 7,843 customers and 16.8 MVA of load.
PSEG-2020-0004 | PSEG | PJM MA | 2020-07-16 | 2020-08-13 | 2020-10-12 | s2318 |  |  | Station equipment at Central Avenue has been in service since 1926 and needs to be addressed. The station building is in poor condition. • The 26kV breakers are original and failure of breakers to operate has resulted in 2 extended station shutdowns. Central Avenue protective relays do not have designated bus protection. • Central Avenue serves roughly 18,300 customers and 24.7 MVA of load.
PSEG-2020-0005 | PSEG | PJM MA | 2020-08-04 | 2020-09-01 | 2020-10-29 | s2355.1 |  |  | The 5015 line in southern New Jersey runs from Red Lion (DPL) to Hope Creek Nuclear Station (PSE&G) and has experienced 9 faults in the past 10 years due to avian activity and lightning strikes, with the two most recent faults occurring in April 2020. The line is currently protected using power line carrier relaying. Additional simulation testing has revealed a more secure and reliable method for fault detection and isolation is required to avoid potential overtrips.
PSEG-2020-0006 | PSEG | PJM MA | 2020-09-01 | 2020-10-06 | 2021-02-10 | s2384 |  |  | Cook Rd is a station in the Belleville area at capacity of 120 MVA. • Cook Rd serves roughly 49,000 customers with a peak load of 145 MVA in 2019.
PSEG-2020-0007 | PSEG | PJM MA | 2020-09-01 | 2020-10-06 | 2020-11-30 | s2385 |  |  | Cuthbert Blvd is a station in the Northern Camden area at capacity of 120MVA. • Cuthbert Blvd serves roughly 33,000 customers with a peak load of 143MVA in 2019.
PSEG-2020-0008 | PSEG | PJM MA | 2020-09-10 | 2020-11-18 |  |  |  |  | Beaverbrook is a station in the Western Camden County area at capacity of 60 MVA. • Beaverbrook serves roughly 22,000 customers with peak load of 70 MVA in 2019.
PSEG-2020-0009 | PSEG | PJM MA | 2020-09-10 | 2020-11-18 |  |  |  |  | Leonia is a station in the eastern Bergen County area at capacity of 120 MVA. Bergenfield is a station in the eastern Bergen County area at capacity of 60 MVA. • Leonia serves roughly 34,800 customers with peak load of 145 MVA in 2019. • Bergenfield serves roughly 19,200 customers with peak load of 72 MVA in 2019.
UGI-2020-0001 | UGI | PJM MA | 2020-09-10 | 2020-11-18 |  |  |  | Koonsville 66kV/13kV Substation | Koonsville66kV/13kV Substation – The two transformer substation constructed in 1967, consists primarily of original equipment (all major components). – Located on a 0.25 acre parcel between two commercial buildings and adjacent to a creek (in the rear). – Concerns relative to public safety due to limited space and associated clearance from substation. – Internal clearances do not meet current NESC requirements. – Access around the substation particularly with the mobile substation is restricted by buildings. – The non-standard design includes minimal infrastructure, clearances and little consideration for expansion and upgrades – Substation is tapped off a networked 66kV line with no highside circuit breaker protection. Distribution transformer protection is single phase fusing. – The substation structure is original wood-pole construction with no 13kV bus. Space does not provide for distribution feeder expansion.
PSEG-2020-0012 | PSEG | PJM MA | 2020-11-18 | 2021-01-14 |  |  |  |  | Albany St is supplied by 26kV circuits with increasing performance problems. • Albany St. Station is at risk in a major storm event. Albany St. is surrounded by flood zone and is inaccessible for an extended period during a flooding event. • Additional capacity is needed in New Brunswick for a new large customer. • Over the past decade, the 26kV supply circuits have seen 17 momentary and 19 extended outages, with total duration of 395 hours. • Albany serves roughly 18 MVA of load.
PSEG-2020-0013 | PSEG | PJM MA | 2020-11-18 | 2021-01-14 |  |  |  |  | Saddle Brook 2H is a station in the Paramus area at capacity of 60 MVA. • Saddle Brook serves roughly 20,124 customers with peak load of 67.6 MVA in 2019. New Milford 1H and 2H is a station in the Paramus area at capacity of 120 MVA. • New Milford serves roughly 33,472 customers with peak load of 131 MVA in 2019.
ACE-2021-0001 | ACE | PJM MA | 2021-02-16 | [5 empty] | Customer proposed facility adding a 30MW load in the Repauno, NJ area. Distribution infrastructure in the area cannot adequately accommodate this load. Current Load: 0 MW Proposed 2023 Load: 30 MW
ACE-2021-0002 | ACE | PJM MA | 2021-02-16 | [5 empty] | Carney’s Point and Pennsgrove Substations are both tapped 69/4kV transformer stations with obsolete and deteriorating 4kV equipment. The Oldmans Substation breaker is experiencing gas leaks and is in need of replacement.. In addition, projected load growth in this region is expected to overload existing distribution infrastructure.
DPL-2019-0001 | DPL | PJM MA | 2019-01-25 | 2021-02-16 |  |  |  |  | Customer has requested a new 138 kV interconnection point off the Mt. Pleasant to Townsend 138 kV line due to load growth within the municipality.
PSEG-2020-0010 | PSEG | PJM MA | 2020-11-18 | 2021-02-16 |  |  |  |  | Elizabeth Substation is supplied by 26kV circuits with increasing performance problems. • Over the past decade, the four 26kV supply circuits have seen 11 momentary and 36 extended outages, with total duration of 1147 hours. • Station equipment at Elizabeth has been in service since 1914 and needs to be addressed. • Historical flooding has compromised some station structures. • Elizabeth serves roughly 7,965 customers and 27.3 MVA of load.
APS-2021-001 | APS | PJM West | 2021-02-17 |  |  |  |  | Sand Fork, Weston, Vens Run 138 kV | Due to the load addition at Vens Run (s2293), subsequent analysis identified a low voltage condition at Weston, Vens Run, and Sand Fork 138 kV substations (0.89 p.u.) for a maintenance outage of the Rider to Vens Run 138 kV line followed by the loss of the Weston 138 kV capacitor.
DOM-2021-0024 | DOM | PJM South | 2021-03-18 |  |  |  |  | Davis Substation | Dominion Energy has identified a need to replace twelve 69kV breakers at Davis Substation due to age and increasing maintenance issues. The breakers in question were manufactured in 1990 and several of this type have experienced the arcing tip breaking and falling off the main moving contact assembly. There is no way to detect this issue without a failure unless it is caught during maintenance. This condition can lead to a catastrophic failure if the arcing tip falls into the breaker and creates a flash or unsuccessful fault interruption
AEP-2021-AP007 | AEP | PJM West | 2021-03-19 |  |  |  |  | Charleston, WV | The 3 mile Chemical – Ward Hollow 46 kV line has two delivery points that are connected via hard taps. The hard taps complicate restoration activities and extend outages. Customers served at the hard taps have communicated concerns regarding continuation of service due to upcoming outages scheduled for ongoing projects at Chemical (B3100, S2348), South Charleston (S2348) and Turner (S2165)
AEP-2021-AP008 | AEP | PJM West | 2021-03-19 |  |  |  |  | Christiansburg, VA | The 13.2 Mvar 69 kV capacitor bank at South Christiansburg station has failed.
AEP-2021-AP009 | AEP | PJM West | 2021-03-19 |  |  |  |  | Carroll County, Virginia | A customer has requested service for the establishment of a new distribution station in anticipation of a future industrial customer(s) located at the Wildwood Commerce Park site in Hillsville, VA. This station is the result of VA House Bill 1840 (HB1840) (Electric Utilities: Pilot Programs for Transmission Facilities Serving Business Parks).
AEP-2021-AP010 | AEP | PJM West | 2021-03-19 |  |  |  |  | Boone County, WV | Both Spruce Laurel and Hampton stations are no longer feeding customers but have equipment connected to the transmission through path.
AEP-2021-AP011 | AEP | PJM West | 2021-03-19 |  |  |  |  | Wayne County, West Virginia | Kenova substation: The 14.4 Mvar 69 kV capacitor bank at Kenova substation has failed.
AEP-2021-AP012 | AEP | PJM West | 2021-03-19 |  |  |  |  | Fayette/Raleigh County, WV | Layland – Molly’s Creek 69 kV, Molly’s Creek – Brooklyn Switch (~8 miles) Circuit is comprised mostly of wood pole structures 1913 vintage structures (98%) Circuit fails to meet 2017 NESC Grade B loading criteria and AEP structural strength requirements 4-bell porcelain insulators do not meet current AEP Standards 32 structures with at least one open condition (38% of the structures) There are 58 structural open conditions affecting poles and crossarms including rot, woodpecker holes and insect damage There are 2 shield wire open conditions related to broken strands, 5 hardware open conditions affecting guys and 2 forestry open conditions related to brush clearance Since 2014, there have been 6 momentary and 5 permanent outages on the Bradley - Layland No. 2A 69 kV circuit Majority of the momentary outages were due to weather including lightning Permanent outages due to vegetation from outside the ROW and lightning Lack of shielding on 28% of the circuit likely contributed to poor lightning performance Outages resulted in approximately 114k customer minutes of interruption Thurmond SS – Claremont 69 kV (~2 miles) Circuit is comprised of wood pole structures 1972 vintage structures (100%) Circuit fails to meet 2017 NESC Grade B loading criteria and AEP structural strength requirements, and fails to meet ASCE structural strength requirements 4-bell porcelain insulators do not meet current AEP Standards 5 structures with at least one open structural condition (17% of the structures) There are 5 structural open conditions related to woodpecker damage and rot and 3 hardware conditions related to cracked insulator assembly and broken guys Outage statistics included in the data above
AEP-2021-AP013 | AEP | PJM West | 2021-03-19 |  |  |  |  | Buchanan County, Virginia | Skeggs Branch substation: 138/69/4 kV Transformer #1 1950s Vintage Transformer , originally manufactured in 1952 The Transformer has elevated levels of Carbon Monoxide, Carbon Dioxide, Ethane, Methane, and Ethylene. There is an indication of overheating faults occurring in the main tank which have further degraded the insulating paper materials. One of the oil cooling pumps has developed a leak. 138kV Circuit Switcher A Mark V type SF-6 filled ( 1970s vintage ) manufactured by S&C. This CS has experienced 37 Fault Ops No gas monitor; sister units on the AEP system have a history of gas loss, interrupter failures, and operating mechanism failures. Relaying Currently, 12 of the 14 relays (86% of all station relays) are in need of replacement. Of these, 11 are of the electromechanical type and 1 static type, which both have no spare part availability and limited fault data collection and retention. In addition, these relays lack of vendor support. Other: The lack of a transformer low side/69kV line exit circuit breaker means that the 138kV circuit switcher operates for both 138kV and 69kV line faults.
AEP-2021-AP014 | AEP | PJM West | 2021-03-19 |  |  |  |  | Buchanan County, Virginia | Line Name: Garden Creek – Skeggs Branch – Richlands 69kV Original Install Date (Age): 1935,1962,1970 Length of Line: ~21 mi Total structure count: 180 Original Line Construction Type: Wood and Lattice Steel Conductor Type: 3/0 ACSR 6/1 (Pigeon), 556,500 CM ACSR 26/7 (Dove), and 336,400 CM ACSR 30/7 (Oriole) Momentary/Permanent Outages: 26 Momentary and 6 permanent Outages CMI (last 5 years only): 0 Line conditions: 42 structures with at least one open structural condition, 23% of the structures on this circuit. 73 structure related open conditions impacting wooden poles, lattice steel towers, crossarms, braces, and filler blocks including rot, bowing, woodpecker holes, insect damage, cracked, split, and heavy rust/corrosion. 1 open conditions related to broken strands 8 hardware related open conditions related to broken or chipped insulators and a buried guy. Other: This circuit is operated normally open at Permac station Lack of sectionalizing capability due to multiple stations (Twin Valley SS, Marvin, Clell) being hard tapped to 69kV Line or operated radially Whetstone Branch is a 3 terminal switching station with no 69 kV line breakers. Only 11.6 miles of this line are currently shielded.
AEP-2021-AP015 | AEP | PJM West | 2021-03-19 |  |  |  |  | Kanawha County, WV | Turner (Starts at Str. 359-203) – Ward Hollow 46 kV Line (~5 miles) Circuit is comprised mostly of steel lattice structures, steel towers and wood poles Originally installed in 1920 Wood pole structures mainly include pre 1970s vintage and 1980s vintage Circuit fails to meet 2017 NESC Grade B loading criteria and AEP structural strength requirements and fails to meet the current ASCE structural strength requirements 8 structures with at least one open condition (30% of the structures) 28 Structural conditions are related to poles and crossarms including rot top, woodpecker and rot heart. 6 shielding/grounding open conditions related to broken/damaged strands Additionally, refer to AEP presentation on pre-1930s steel lattice lines, linked above Since 2015, there have been 5 momentary and 11 permanent outages on the Turner – Ward Hollow 46 kV circuit Momentary outages were due to wind, lightning and animal bus causes Permanent outages due to lightning, vegetation from outside the ROW, wind, station relay, distribution, line conductor and station arrestor causes Outages resulted in approximately 852 customer minutes of interruption for wholesale customers
AEP-2021-IM005 | AEP | PJM West | 2021-03-19 |  |  |  |  | Industrial Park – Spy Run 34.5kV | Industrial Park – Spy Run 34.5kV ~4.2 Miles Wood pole line originally constructed in 1965 45 structures have at least one open condition (37% of line) including Rot Top, Insect Damage and Woodpecker holes 18 structures were assessed by an aerial drone and 12 assessed by ground crew. 6 structures had heart rot, 12 structures had insect/woodpecker damage. 121,563 CMI over the past 5 years with 2 outages Structures do not meet 2017 NESC Grade B loading criteria, do not meet current AEP structural strength requirements, and do not meet the current ASCE structural strength requirements.
AEP-2021-IM013 | AEP | PJM West | 2021-03-19 |  |  |  |  | North Bluffton 69kV Load Addition | North Bluffton 69kV City of Bluffton has requested an expansion to their delivery point to serve a new 5MW load increase by November 1, 2021
AEP-2021-OH009 | AEP | PJM West | 2021-03-19 |  |  |  |  | Defiance, Ohio | Lockwood Road 138 kV Station Circuit Breakers A: Manufactured Date: 1982 Interrupting Medium: (SF6) Fault Operations: Number of Fault Operations: 85 Manufacturer recommended Number of Operations: 10 Additional Breaker Information: The expected life of the bushing gaskets and door inspection port seals is 25 years, this breaker has surpassed this age. Seals that are no longer adequate can cause SF6 leaks to become more frequent. The vendor provides no support or manufactures spare parts for this family of circuit breakers. Relays: Currently, 30 of the 31 relays (97% of all station relays) are in need of replacement. 25 of these are of the electromechanical type and 2 of the static type which have significant limitations with regards to spare part availability and fault data collection and retention. In addition, these relays lack of vendor support. There are also 3 microprocessor based relays commissioned in 2009 and have unsupported firmware Operational Flexibility and Efficiency The Richland line terminal has a MOAB instead of a CB. This is a tie-line to First Energy. The bypass switch on CB-B complicates the bus protection. It is an operational challenge due to the City of Bryan having generation as well as a second source from the First Energy system (through Richland). Bypasses create protection reliability concerns. The capacitor at Lockwood Rd bank causes voltage quality issues for City of Bryan when either of the 138 kV sources into Lockwood Road are out of service due to the size of the bank. Customer Service The existing Station is not expandable in its current configuration. There has been significant interest from large industrial load (future) to construct in this area, and specifically to connect to this station.
AEP-2021-OH010 | AEP | PJM West | 2021-03-19 |  |  |  |  | Richland, Ohio | Howard Station: Circuit Breaker: K Breaker Age: 1959 Interrupting Medium: (Oil) Fault Operations: Number of Fault Operations: 27 Manufacturer recommended Number of Operations: 10 Additional Oil Filled Breaker Information: These breakers lack oil containment; oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. Circuit Breakers: A, B, & E Breaker Age: 1990: A, B, & E Interrupting Medium: (SF6) Fault Operations: Number of Fault Operations: A 13, B 30, & E 13 Manufacturer recommended Number of Operations: 10 Additional 145-PA model Breaker Info: As of May 11, 2020, there have been 437 recorded malfunctions of this 145-PA model family on the AEP System. The most common issues documented are related to loss of SF6 gas and mis-operations. The expected life of the bushing gaskets and door inspection port seals is 25 years; all four of these units have reached this age. Seals that are no longer adequate can cause SF6 leaks to become more frequent. The manufacturer provides no support for this family of circuit breakers, and no longer manufactures spare parts. Circuit Switcher: CS-CC Switcher Age: 2000 Interrupting Medium: (SF6) Additional SF6 Mark V Type Information: The Mark V family of circuit switchers have no gas monitoring capability and have experienced 110 malfunctions from May 2000 to August 2019. Failed operational components including high contact resistance, gas loss, and interrupter failure represent half of these malfunctions. Relays: Currently, 107 of the 122 relays (88% of all station relays) are in need of replacement. 83 of these are of the electromechanical type and 8 of the static type which have significant limitations with regards to spare part availability, fault data collection, and data retention. In addition, these relays lack of vendor support. There are also 16 microprocessor based relays commissioned between 2006 and 2011 that may have firmware that is unsupported. The existing RTU installed at Howard Substation is a legacy GE D200MEII/Ethernet unit that has no spare parts availability or vendor support.
AEP-2021-OH011 | AEP | PJM West | 2021-03-19 |  |  |  |  | Washington & Morgan Counties, Ohio | Line Name: Muskingum – South Rokeby 69kV Original Install Date (Age): 1965 Length of Line: ~21.3 mi Total structure count: 164 Original Line Construction Type: Wood Conductor Type: 4/0 ACSR 6/1, 336,400 CM ACSR 18/1, and 336,400 CM ACSR 30/7 Momentary/Permanent Outages and Duration:10 Momentary and 2 Permanent Outages CMI: 315,751 (past five years) Line conditions: 48 structures with at least one open condition, 29% of the structures on this circuit. 45 structure related open conditions impacting wooden poles, crossarms, braces, and filler blocks including rot, bowing, woodpecker holes, insect damage, cracked, split, and rot top 12 open conditions related to conductor issues including broken strands 12 hardware/shielding issues including open conditions related to burnt, broken, or chipped insulators. Structure Age: 72% 1960’s, 15% 1970, 13% 1980’s or newer Other: The line shielding angle does not meet AEP’s current shielding angle requirements Line does not meet current NESC Grade B loading criteria or AEP’s current structural strength requirements. Washington Co-op’s Bartlett Station is served radially from this line (~ 5.09 miles) with limited sectionalizing ability.
AEP-2021-OH012 | AEP | PJM West | 2021-03-19 |  |  |  |  | Holmesville, Ohio | Buckeye is requesting, on behalf of Holmes- Wayne Electric co-op, a new 138kV delivery point on the West Millersburg- Wooster 138kV Circuit by August 2023. Anticipated load is 4.4 MW.
AEP-2021-OH013 | AEP | PJM West | 2021-03-19 |  |  |  |  | George Washington-Kammer (Marshall County, WV) | George Washington-Kammer 138kV circuit (6.9 miles) The line consist of 6.7 miles of original (1956) lattice towers and conductor (6-wired 636 ACSR). There is 0.2 miles of newer construction that is in adequate condition (outside the substation at each end). The shield wire design does not meet current shielding angle requirements. There are currently 14 hardware-based open conditions on the line (primarily insulator damage), 1 conductor condition (broken strands), and 1 structure condition. Some of the steel lattice towers show heavy rusting and corrosion. The original insulator strings show significant residue/contamination, leading to risk of flashovers and circuit outages. Hook attachments freely move and wear through the hangers. This wear results in the loss of steel section over time. That section loss reduces the strength of the connection which can result in premature failure. There is evidence of hole elongation and the amount of steel left in the hanger holding up the suspension insulators is thin.
AEP-2021-OH014 | AEP | PJM West | 2021-03-19 |  |  |  |  | Franklin County, OH | Customer Service: A customer has requested transmission service at a site just southeast of AEP’s existing Hayden station in Hilliard, OH. The customer has indicated an initial peak demand of 64 MW with an ultimate capacity of up to 256 MW at the site.
AEP-2021-OH015 | AEP | PJM West | 2021-03-19 |  |  |  |  | St. Clairsville, Ohio | The Highland Terrace 69-12kV distribution substation north of St. Clairsville, Ohio is a unique 1975-vintage modular station (“station in a box”). The indoor station had a major failure in August 2019 and has been bypassed with a mobile since that time. Circuit Switcher CS-AA (69kV) Breaker Age: 1973 Interrupting Medium: (Vacuum) Additional Information: This switcher has failed and is no longer in working condition. The vacuum bottles have failed and there are no replacement parts available for this unit. The vacuum interrupter bottles have suffered flashovers and the switch is currently inoperable. Transformer: 69/12 kV TR-1 Age: 1975 The dielectric strength and interfacial tension are trending downwards which can indicate an increase in particles within the oil, decreasing the dielectric strength of the oil to withstand fault events, which can damage the paper insulation. The values of dielectric strength, IFT and power factor indicate the dielectric strength of the insulation system (oil and paper) are in poor condition, which impairs the unit’s ability to withstand electrical faults. No oil containment There are no surge arrestors installed, which does not meet AEP station standards Relays: 22 relays, implemented to ensure the adequate protection and operation of the substation. Currently, 22 of the 22 relays (100% of all station relays) are in need of replacement. All 22 of these are of the electromechanical type which have significant limitations with regards to spare part availability and fault data collection and retention. In addition, these relays lack of vendor support. Other: The metal building has various leaks and rust. The 69kV & 12kV underground cables are direct-bury and original to the station (1975). There is no perimeter fence for the modular station, leaving it vulnerable to vandalism or theft. There are identified needs on several 12 kV breakers (CB A & B). Over the past 5 years, equipment failures have caused 421,724 customer-minutes-of-interruption (CMI).
AEP-2021-OH017 | AEP | PJM West | 2021-03-19 |  |  |  |  | Lawrence County, OH | A customer has requested 69kV service in Lawrence County, Ohio. This request is on the Dow Chemical – Highland 69 kV line and the in-service date is February 2022. The anticipated peak load is approximately 22 MW.
AEP-2020-AP027 | AEP | PJM West | 2020-04-20 | 2021-03-19 |  |  |  | Roanoke & Lynchburg, VA Area | Reusens-Roanoke 138 kV Double Circuit Line Asset (43 mi.) Installed between 1926 and 1933 using double circuit steel lattice towers Recent field assessments have identified severe ovalization of holes at hanger bar connections and severe cross arm and hanger rusting as well as uniform corrosion, pitting, and deformation of steel members below grade. Evidence of steel corrosion at joints and on upper steel members was also documented. Ferrous clamps are present on this line asset; these types of clamps can cause accelerated degradation of conductor at connection points due to excess heat generated even when operated at acceptable, rated levels. From 2014-2018, there have been 55 momentary and 12 permanent outages on the four circuits that comprise the Reusens-Roanoke line Cloverdale-Roanoke 138 kV Circuit* From 2014-2018, 8 momentary and 1 permanent outage occurred resulting in 276,350 customer minutes of interruption impacting 69 MVA of peak load Permanent outage(s) were caused by: Vegetation Fall-In (1) Cloverdale-Reusens 138 kV Circuit* From 2014-2018, 28 momentary and 6 permanent outages occurred resulting in 1,467,704 customer minutes of interruption impacting 39 MVA of peak load Permanent outage(s) were caused by: Lightning (4), Tree Removal (1), Vegetation Fall-In (1) Moseley-Roanoke 138 kV Circuit From 2014-2018, 9 momentary and 1 permanent outage occurred Permanent outage(s) were caused by: Lightning (1) Moseley-Reusens 138 kV Circuit From 2014-2018, 10 momentary and 4 permanent outages occurred impacting 44 MVA of load (Town of Bedford) Permanent outage(s) were caused by: Lightning (2), Vegetation Fall-In (1), Field Error (1)
AEP-2020-AP033 | AEP | PJM West | 2020-05-22 | 2021-03-19 |  |  |  | Roanoke, VA Area | 138/69/12 kV Transformer #5 1981 Vintage Transformer Elevated levels of carbon monoxide, carbon dioxide and hydrogen indicate excessive levels of decomposition of the paper insulating materials. 138 kV Circuit Switchers BB and CC Both are 1990’s vintage The Mark V family of circuit switchers have no gas monitor and currently in-service units on the AEP system have experienced 110 malfunctions from May 2000 to August 2019. Failed operational components including high contact resistance, gas loss, and interrupter failure represent half of these malfunctions. Two malfunctions of note were catastrophic equipment failures involving failures to trip. 138 kV Capacitor Bank CC and 34.5 kV Capacitor Bank AA Leaking around bushings on both banks 6 cans are failed on bank CC 69 kV Circuit Breakers U and V 1970’s Vintage Circuit Breakers These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require Circuit breaker U has each exceeded the manufacturer’s designed number of full fault operations (12) Relaying Roanoke Substation currently deploys 103 relays, implemented to ensure the adequate protection and operation of the substation. Currently, 79 of the 103 relays (77% of all station relays) are in need of replacement. There are 50 electromechanical and 8 static which have significant limitations with regards to fault data collection and retention. These relays lack vendor support and have little to no access to spare parts. There are 3 DPU microprocessor type relays on the three distribution breakers. The DPU relays pose a potential safety risk to persons performing breaker operation because the DPUs are mounted directly on the circuit breaker without a delay for opening and closing the breaker. There are 18 microprocessor relays that utilize legacy firmware. Pilot Wire Pilot wire relaying exists on the Campbell Ave. 69 kV, Roanoke 69 kV and Campbell Ave 34.5 kV circuits TFS lacks adequate crew training and experience on handling pilot wire; only a small number of crews are available with necessary experience to perform corrective maintenance High corrective maintenance costs are incurred (P&C, line, forestry, build roads, etc.) High-Side Transformer Protection No automatic high-side protection exists on transformer #5 or #2 Both are directly connected to 138 kV bus #2, which would operate five 138 kV circuit breakers for a transformer fault
AEP-2020-AP034 | AEP | PJM West | 2020-05-22 | 2021-03-19 |  |  |  | Centerville, VA Area | 69 kV Circuit Breaker B 1970’s Vintage Circuit Breaker Oil filled breaker without oil containment. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. This circuit breaker, has exceeded the manufacturer’s designed number of full fault operations (108) High-side Transformer MOAB Ground Switch (138/69/12 kV T1) is used for high-side transformer protection There is a three terminal line configuration through the Town of Bedford 69 kV loop. The flip-flop configuration connection to the double circuit 138 kV line that runs adjacent to the station is a source of operational and protection challenges when faults occur. Relaying Centerville Substation currently deploys 26 relays, implemented to ensure the adequate protection and operation of the substation. Currently, all 26 of the relays (100% of all station relays) are in need of replacement. There are 21 of the electromechanical which have significant limitations with regards to fault data collection and retention. These relays lack vendor support and have little to no access to spare parts. Also, the remaining 5 relays that are microprocessor based from utilize legacy firmware.
AEP-2020-AP029 | AEP | PJM West | 2020-04-20 | 2021-03-19 |  |  |  | Johnson County, KY | Line Name: Kenwood – Van Lear 46kV Original Install Date (Age): 1969 Length of Line: 1.77 mi Total structure count: 11 Original Line Construction Type: Wood Conductor Type: 336,400 ACSR 26/7 Line conditions: 3 of the 11 structures have conditions that comprise 27% of the line section. Open conditions include: rot and woodpecker damage. Kenwood Station is currently radially fed with a peak load near 22 MVA. Van Lear Switch: The switches at Van Lear have been tagged as inoperable and unsafe to operate. The old hydraulic type mechanism on these switches does not operate properly, arcing horns are burnt off, and operating rod supports are damaged.
AEP-2020-IM024 | AEP | PJM West | 2020-11-20 | 2021-03-19 |  |  |  | Illinois Road Transformer | 138/69/12kV Transformer 1 Manufactured in 1980 Transformer is showing elevated moisture levels, low levels of Interfacial Tension and an increasing trend in Power Factor. This level of moisture is an indication of gasket leaks and breakdown in oil or paper insulation. The low level of Interfacial Tension is an indication acid has coated the insulation and sludge is ready to deposit within the main tank. The upward trend in PF indicates that there is an increase in particles in the oil.
AEP-2020-OH045 | AEP | PJM West | 2020-11-20 | 2021-03-19 |  |  |  | Columbus, Ohio | AEP Ohio has requested installation of a second 138/13.8 kV transformer at Fifth Ave Station to address increased loading on the existing distribution feeders at the station due to load growth in the area. Fifth Avenue station has limited transferability and serves approximately 7,000 customers via a single transformer in an urban environment. AEP Ohio has also expressed concerns over the amount of exposure that existing feeders out of Hess station are subject to in the area.
ComEd-2021-001 | ComEd | PJM West | 2021-03-19 |  |  |  |  | 138 kV Line 8604 | 138 kV line 8604 is currently normally open at Bradley The Bradley / Kankakee area serves 335 MW of load from two lines Line 8604 has 3.5 miles of 636 kCMIL ACSR conductor on 40 year old wood H-frames.
ComEd-2021-002 | ComEd | PJM West | 2021-03-19 |  |  |  |  | 138 kV Line 0708 | 138 kV line 0708 is directly connected to center bus at State Line substation without a circuit breaker. A fault on line 0708 separates the 2 other 138 kV buses.
Dayton-2021-002 | Dayton | PJM West | 2021-03-19 | [5 empty] | DP&L d/b/a AES Ohio Distribution is planning for a 5MVA load increase from a new development near the Montgomery County Fairgrounds. Currently, this area is served via the Eaker Substation and the distribution circuits out of Eaker are heavily loaded and would be over 100% with the addition of this new load. This general area has experienced growth in recent years and the load addition of 5MVA will require additional capacity. Additionally, the Tait substation provides distribution services to The University of Dayton and a local critical facility through a 2.0+ mile long URD cables. The cables have historically been difficult to work with during outages and will need future upgrades. It is essential that a new source is located near the load center and critical customer to reduce exposure to cable faults and serve the growing load. Additional circuit ties exist in the area but do not have enough capacity for significant load transfers and would further limit the ability to conduct circuit switching during outages.
DEOK-2021-003 | DEOK | PJM West | 2021-03-19 |  |  |  |  | Fairfield-Nilles | A pole on the 69 kV circuit from Fairfield to Nilles had failed inspection. This pole supports a switch that limits the circuit. The pole shows signs of decay and base rot, and has been on the watch list since 2015.
DEOK-2021-004 | DEOK | PJM West | 2021-03-19 |  |  |  |  | North Bend | Duke Energy Distribution has asked for a new delivery point in North Bend, OH. The distribution transformers that serve this area from Neumann and Sayler Park are peaking at 100% of rated capacity. Several large residential developments are planned or are currently under construction in this area.
DEOK-2021-005 | DEOK | PJM West | 2021-03-19 |  |  |  |  | Newtown | Duke Energy Distribution has asked for additional capacity at Newtown substation. Obsolete 4 kV distribution facilities at Madeira, Milford, Clertoma and Terrace Park are being retired. 10 MVA of 13 kV capacity is required.
EKPC-2021-007 | EKPC | PJM West | 2021-03-19 |  |  |  |  | Speedwell Road New Customer Load | A new customer has requested a new delivery point for a winter peak demand of 28.5 MW and 1.5 MW summer peak by 7/1/2022. The new delivery point is located in Madison Co, KY approximately 5.5 miles northeast from EKPC’s Crooksville distribution substation. The existing distribution infrastructure is not capable of serving this request.
EKPC-2021-008 | EKPC | PJM West | 2021-03-19 |  |  |  |  | Taylorsville Distribution Substation | The Taylorsville distribution substation was built in 1946. This station is currently served from LG&E/KU’s Bardstown-Finchville 69 KV transmission circuit. This station has numerous issues associated with aging/condition, site location, and accessibility. The station has a narrow driveway with a 90 degree turn. Extremely small station footprint with minimal space to maneuver around the equipment. High side switch and porcelain lightning arrestors are at end of life. There is no metering bypass, or bypass buss in the low bay, which prolongs restoration. The distribution transformer is inconveniently located under the high side bus which creates prolonged maintenance outage time.
EKPC-2021-009 | EKPC | PJM West | 2021-03-19 |  |  |  |  | Three Links Jct. – Three Links 69kV | The 9.61 mile, Three Links Jct.-Three Links 69 KV transmission line is 63 years old. This line has condition issues such as conductor steel core and static wire deterioration, rusting, pitting and broken strands. Based on this information, the EKPC Reliability team has concluded that this line is at or near end of life and should be addressed due to the condition.
EKPC-2021-010 | EKPC | PJM West | 2021-03-19 |  |  |  |  | Goddard - Charters 69 KV | The 17 mile, Goddard - Charters transmission line is 69 years old. Testing from the LineVue robot from Kinectrics Corporation deemed the phase and static wire condition as marginal. The testing identified instances of rusting, pitting, and broken strands. Based on this testing information, the EKPC Reliability team has concluded that this line should be addressed due to the condition assessment.
EKPC-2021-011 | EKPC | PJM West | 2021-03-19 |  |  |  |  | Beattyville - Tyner 69 KV | The 29.29 mile, Beattyville-Tyner transmission line is 65 to 66 years old. Testing from the LineVue robot from Kinectrics Corporation deemed the phase and static wire condition as poor. The testing identified instances of rusting, pitting, and broken strands. Based on this testing information, the EKPC Reliability team has concluded that this line should be addressed due to the condition assessment.
PN-2021-002 | PN | PJM MA | 2021-03-18 | [5 empty] | New Customer Connection - A customer requested 46 kV service for load of approximately 12 MW near the Greenwood – Tipton 49 kV line. Requested inservice date is 7/2021.
DOM-2021-0003 | DOM | PJM South | 2021-04-06 | [5 empty] | DEV Distribution has submitted a DP Request to add transformers at Takeoff Substation to support a new datacenter campus in Fairfax County with a total load in excess of 100 MW. The new station will also support existing load in the immediate area
DOM-2021-0018 | DOM | PJM South | 2021-04-06 | [5 empty] | DEV Distribution has submitted a DP Request to add a 2nddistribution transformer at Nokesville Substation in Prince William County. The new transformer is being driven by data center load growth in the area
DOM-2021-0019 | DOM | PJM South | 2021-04-06 | [5 empty] | DEV Distribution has submitted a DP Request to add a 2nddistribution transformer at Hamilton Substation in Loudoun County. The new transformer is being driven by contingency loading for loss of the existing transformer
DOM-2021-0020 | DOM | PJM South | 2021-04-06 | [5 empty] | NOVEC has submitted a DP Request for a new substation (Hourglass) to serve a data center complex in Prince William County with a total load in excess of 100 MW
DOM-2021-0032 | DOM | PJM South | 2021-04-06 | [5 empty] | DEV Distribution has submitted a DP Request to add the 3rd and 4th distribution transformers at Davis Drive Substation in Loudoun County. The new transformers are being driven by continued data center load growth in the area
DOM-2021-0035 | DOM | PJM South | 2021-04-06 | [5 empty] | DEV Distribution has submitted a DP Request to upgrade the distribution transformer at Plaza Substation in the City of Richmond. The transformer upgrade is being driven by a poor Transformer Health Assessment (THA) score
DOM-2021-0025 | DOM | PJM South | 2021-04-06 | [5 empty] | Dominion Energy has identified a need to replace approximately 2.7 miles of 230kV Line #239 (Lakeview to Hornertown) which includes the double circuit segment with Line #2141 (Carolina to Lakeview) based on the Company’s End of Life criteria
DOM-2021-0026 | DOM | PJM South | 2021-04-14 | [5 empty] | Dominion Energy has identified a need to replace approx. 14.6 miles of 115kV Line #83 from Craigsville to the junction where 115kV Line #83 transitions to double-circuit with 230kV Line #293
DOM-2021-0027 | DOM | PJM South | 2021-04-14 | [5 empty] | Dominion Energy has identified a need to replace the entire 12.6 miles of 115kV Line #5 (Bremo to Cunningham DP) based on the Company’s End of Life criteria
DOM-2021-0030 | DOM | PJM South | 2021-04-14 | [5 empty] | Dominion Energy has identified a need to replace approximately 12.4 miles of 115kV Line #96 (Everetts to Parmele) based on the Company’s End of Life criteria
ACE-2021-0003 | ACE | PJM MA | 2021-04-14 | [5 empty] | Beckett Substation is currently configured as two (2) tapped 69/12kV transformers off the 69kV Churchtown-Paulsboro line with no high side breakers. Beckett Substation has experienced six (6) bus interruptions since 2018
ODEC-2021-001 | ODEC | PJM MA | 2021-04-14 | [5 empty] | Protection and Control of the existing transmission system relies on over current and distance relays. • Existing generation approximates load in multiple areas. • Breaker failure backup relaying is currently at the next station upline and increases line clearing times. • High speed, reliable communications does not exist between stations. • Communications with PJM and to SCADA systems are being provided by third parties. ODEC wishes to take over these comms as one third party is planning on retiring existing equipment. • Existing generators at Cheriton and Tasley presently detect islanding indirectly through abnormal frequency and voltage.
PSEG-2021-0002 | PSEG | PJM MA | 2021-04-14 | [5 empty] | Ridgefield 1H is a station in Bergen County operating above its capacity of 60 MVA. • Ridgefield Substation 1H serves roughly 23,000 customers with a load of 66 MVA in 2020.
PSEG-2021-0003 | PSEG | PJM MA | 2021-04-14 | [5 empty] | • A large customer has requested service for nearly 13MW of load to be in service by July of 2023.
AEP-2021-AP016 | AEP | PJM West | 2021-04-16 | [5 empty] | Capitol Hill – Mink Shoals 69 kV (~3.1 miles) Circuit is comprised primarily of original vintage wood structures (1928) Conductor utilized is comprised primarily of 1979 vintage 4/0 ACSR, 1928 vintage 3/0 ACSR, and 1980 vintage 795,000 CM ACSR conductors. Circuit fails to meet 2017 NESC Grade B loading, current AEP structural strength requirements and current ASCE structural strength requirements Since 2015, there have been 11 momentary and 4 permanent outages on the Capitol Hill – Mink Shoals 69kV Circuit. The momentary outages were attributed to lightning (5), wind (2), unknown (2), animal bus (1), and other station bus operation (1) causes. The permanent outages were attributed to lightning (1), underground line conductor failure (1), vegetation fall-in from outside of the AEP ROW (1), and failed station protection system equipment (1) causes. The permanent outages caused 656k minutes of interruption for 2,420 customers at Mink Shoals Substation. 6 structures with at least one open condition (12% of the structures) 8 open structural conditions affecting poles and crossarms including damaged, rot top, woodpecker damaged, insect damaged, and rot heart conditions. 3 open shielding conditions related to worn shield wire. 2 open hardware conditions related to broken insulators. 1 open ROW condition related to a slip. Roughly 30% of the structures had some sort of decay beyond normal weather conditions.
AEP-2021-AP017 | AEP | PJM West | 2021-04-16 | [5 empty] | APCO Distribution has requested a new distribution station supporting West Virginia Business Ready Sites Program (House Bill 144) located in Raleigh County, West Virginia. Summer projected load: 16 MVA Winter projected load: 16 MVA.
AEP-2021-AP018 | AEP | PJM West | 2021-04-16 | [5 empty] | A customer has requested a new delivery point located in Kanawha County, West Virginia. Summer projected load: 7 MVA Winter projected load: 7 MVA.
AEP-2021-IM003 | AEP | PJM West | 2021-04-16 | [5 empty] | Riverside – Hartford 138kV line: 16.85 miles of mostly 1957 wood H-Frame construction Conductor is 397 MCM ACSR There are 48 structures with open conditions (36% of line). 40 of these are structure related affecting the crossarm, pole, or X-brace including rot, corrosion, cracked, woodpecker, and disconnected conditions. Additional assessment identified the following: 15 structures were subject to some level of decay above normal weathering 10 had crossarm decay 9 had ground line decay 4 had broken/flashed insulators 64% of structures assessed had some level of decay
AEP-2021-IM010 | AEP | PJM West | 2021-04-16 | [5 empty] | Lincoln Tap 138kV ~3.65 Miles Steel lattice double circuit 397 ACSR construction with all 20 structures original from 1947 9 open hardware conditions on 7/20 structures Insulator equipment and hooks with moderate wear 50% of the towers had flashed insulator strings Corrosion on insulator caps & pins
AEP-2021-IM014 | AEP | PJM West | 2021-04-16 | [5 empty] | Deer Creek – Hartford City 69 kV (vintage 1967): Length: 17.67 Miles Original Construction Type: Wood pole structures with cross arm construction and vertical post insulators.Jonesboro – Gas City 34.5 kV (vintage 1969): Length: 1.01 Miles Original Construction Type: Wood pole structures Original Conductor Type: 336.4 ACSR 18/1 Merlin (0.65 mi, vintage 1969) 3/0 Copper 7 (0.36 mi, vintage 1969) Number of open conditions: 12 Open conditions include: Cross arm or pole with split rot conditions, knee/vee brace with loose conditions, broken guy strain insulator and right of way encroaching buildings. Total structure count: 34 (original vintage) Deer Creek – Alexandria 34.5 kV (vintage 1968): Length: 2.19 Miles Original Construction Type: Wood pole structures Original Conductor Type: 556.5 kCM ALUM/1250 19 Dahlia Number of open conditions: 7 Open conditions include: Cross arm or pole with rot top conditions, stolen ground lead wires and improperly installed shield wire. Total structure count: 61, with 60 dating back to original installation. Original Conductor Type: 336.4 kCM ACSR 18/1 Merlin (18.17 mi, vintage 1967) 3/0 Copper 7 (30COP) (2.24 mi, vintage 1967) Momentary/Permanent Outages: 21 total outages: 10 (Momentary), 11 (Permanent). 5 Year CMI: 67,818 Number of open conditions: 4 Open conditions include: Cross arm or pole with split and woodpecker conditions and broken or missing ground lead wire. Based on the ground crew assessment roughly 28% of the structures had advanced levels of decay on the poles Total structure count: 378 with 366 dating back to original installation.
AEP-2021-IM015 | AEP | PJM West | 2021-04-16 | [5 empty] | Hartford – South Haven 69kV line: 18.68 miles of mostly 1966 wood pole Conductor is 336.4 ACSR Since 2015 there have been 20 momentary and 4 permanent outages. 4,984,780 CMI from 2015-2020 Structures fail NESC Grade B, AEP Strength requirements and ASCE strength requirements There are 90 structures with open conditions (29% of line). 52 of these are structure related including pole rot, split and woodpecker damage
AEP-2021-OH020 | AEP | PJM West | 2021-04-16 | [5 empty] | Circuit Breakers: A & B Breaker Age: 1952: A & B Interrupting Medium: (Oil) Additional Oil Filled Breaker Information: These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. Note: the most recent PJM short circuit case shows these breakers may be over-dutied. AEP Operations is taking steps to ensure safe operation of these breakers until they are replaced
AEP-2021-OH023 | AEP | PJM West | 2021-04-16 | [5 empty] | Problem Statement: Line Name: Howard- Fostoria 138kV Original Install Date (Age): 1928 Length of Line: 45.34 miles Total structure count: 264 Original Line Construction Type: Steel Lattice Conductor Type: 397 CM ACSR 30/7 Outage History (last 5 years): 11 momentary and 2 permanent Condition Summary Number of open conditions: 126 Open conditions include: bent structure lacing, rusting, broken/loose/missing conductors, broken/burnt/chipped/insulators, bent/broken/burnt insulator assemblies and hardware, and broken/loose/worn shield wire. Additional Notes: PJM Baseline Project b3249 will rebuild approximately ~10 miles of this line between Chatfield and Melmore 410MW of planned generation on this line in the IPP queue.
AEP-2021-OH024 | AEP | PJM West | 2021-04-16 | [5 empty] | Line Name: Bucyrus – Howard No.1 69kV Original Install Date (Age): 1948 Length of Line: 18.05 miles Total structure count: 413 Original Line Construction Type: Wood 14 % of structures rehabbed since installation Wood Cross Arms Conductor Type: 3/0 Copper 7 conductor Outage History (past 5 years) 7 momentary and 2 permanent outages with an average duration of 5.37 hours CMI: 60,120 Condition Summary Number of open conditions by type / defects / inspection failures: 78 Ground lead wire missing, stolen or broken, structure related conditions affecting the cross arm or pole including rot, split or woodpecker holes, contaminated or broken insulator hardware Number of Customers at Risk: 331, 11.527 MVA
ComEd-2021-003 | ComEd | PJM West | 2021-04-16 | [5 empty] | New customer is looking for transmission service in Hoffman Estates. Initial loading is expected to be 24 MW in June 2023 with an ultimate load of 96 MW by the end of 2027.
Dayton-2021-003 | Dayton | PJM West | 2021-04-16 | [5 empty] | The existing 30.88-mile 69kV transmission line (6602) from Hutchings-Germantown-Gratis-Camden-Crystal was primarily constructed using wood pole, cross-arm and brace design in 1964. This line provides transmission and distribution level service to 5 different substations serving approximately 11,500 customers in Montgomery and Preble Counties totaling approximately 33MW of load. A fault occurring anywhere on this line will result in at least a temporary outage and possible permanent outage to all 11,500 customers. -This line is one of the worst performing 69kV transmission lines in the Dayton zone. The line has experienced 25 outages (3 permanent and 22 momentary) since 2016. Equipment related issues are the primary cause of permanent outages on the line and weather has been the primary cause of momentary issues. -There are two existing automatic sectionalizing switches at Germantown to help reduce outage time, but the switches have not operated reliably during outage conditions due to alignment issues and the switches are not centrally located on the circuit.
DEOK-2021-006 | DEOK | PJM West | 2021-04-16 | [5 empty] | Brown TB1 is a 138/69/34 kV 3-winding transformer. The tertiary winding is connected to a 34 kV distribution bus. This old design exposes the transmission transformer to faults from the distribution system.
EKPC-2021-012 | EKPC | PJM West | 2021-04-16 | [5 empty] | The 1.61 mile, Clay Village 69 KV transmission tie line to LG&E/KU is 70 years old. This line has condition issues such as conductor steel core and static wire deterioration, rusting, pitting and broken strands. Based on this information, the EKPC Reliability team has concluded that this line is at or near end of life and should be addressed due to the condition.
EKPC-2021-013 | EKPC | PJM West | 2021-04-16 | [5 empty] | The 19.9 mile, Headquarters-Murphysville 69 KV transmission line is 66 years old. This line has condition issues such as conductor steel core and static wire deterioration, rusting, pitting and broken strands. Based on this information, the EKPC Reliability team has concluded that this line is at or near end of life and should be addressed due to the condition.
EKPC-2021-014 | EKPC | PJM West | 2021-04-16 | [5 empty] | The 14.2 mile, Peyton Store – Liberty Junction 69 KV transmission line is 67 years old. Testing from the LineVue robot from Kinectrics Corporation deemed the phase and static wire condition as unacceptable. The testing identified instances of rusting, pitting, and broken strands. Based on this testing information, the EKPC Reliability team has concluded that this line is at or near end of life and should be addressed due to the condition assessment.
EKPC-2021-015 | EKPC | PJM West | 2021-04-16 | [5 empty] | The 12.3 mile, Maytown Tap-Hot Mix Road Tap 69 KV transmission line is 62 years old. Testing from the LineVue robot from Kinectrics Corporation deemed the phase and static wire condition as unacceptable. The testing identified instances of rusting, pitting, and broken strands. Based on this testing information, the EKPC Reliability team has concluded that this line is at or near end of life and should be addressed due to the condition assessment.
EKPC-2021-016 | EKPC | PJM West | 2021-04-16 | [5 empty] | The 22.09 mile, KU Carrollton - Bedford transmission line is 61 to 66 years old. This line section has continued to show up on EKPC’s list of Worst Performing Areas for several years, and it is currently the #5 worst performing line. Testing from the LineVue robot from Kinectrics Corporation deemed the phase and static wire condition as poor to marginal. The testing identified instances of rusting, pitting, and broken strands. Based on this testing information, the EKPC Reliability team has concluded that this line is near end of life and should be addressed due to the condition assessment
EKPC-2021-017 | EKPC | PJM West | 2021-04-16 | [5 empty] | The South Fork Distribution Substation is 65 years old, and does not meet current EKPC design standards. The station has the following issues: • limited space with no access to equipment on two sides of the station. • Cap-and-pin insulators, which are a safety and reliability concern. • Does not have the EKPC standard metering bypass switching or low bay transfer schemes, which causes additional outage time and creates a heightened safety risk when taking equipment out of service for maintenance activities. • Several foundations in the station are crumbling. • The elevation change and drainage around the station has caused multiple wash outs of gravel from the station and driveway. • The site entrance is very steep making it difficult to navigate.
AEP-2021-AP015 | AEP | PJM West | 2021-04-19 | [5 empty] | Capitol Hill - Chemical 46kV Circuit (~10.9 miles). Circuit is comprised mostly of vintage wood pole structures. Original vintage wood structures from 1924, 1964 and 1928 The Capitol Hill – Chemical 46kV Line use primarily 1924 vintage 1/0 Copper conductor. The circuits fails to meet 2017 NESC Grade B loading criteria, AEP structural strength requirements and ASCE structural strength requirements Since 2015, there have been 8 momentary and 10 permanent outages on the Capitol Hill – Chemical 46kV Circuit. The momentary outages were attributed to lightning (4), wind (1), distribution (1), vehicle accident (1), and unknown (1) causes. The permanent outages were due to vegetation fall-in from outside of the AEP ROW (8), lightning (1), and wind (1) causes. These outages caused 3.1M minutes of interruption for customers at Guthrie Substation. Currently, there are 38 structures with at least one open structural condition, which relates to 38% of the structures 88 structural open conditions affecting poles, crossarms, and knee/vee braces including rot, woodpecker holes, broken, split, damaged, and cracked conditions. 8 open shielding or grounding conditions related to worn or damaged shield wire and broken or missing ground wire leads. 3 open hardware conditions related to missing or worn shield wire hardware and broken guys. 1 open ROW condition related to a slip. Guthrie Tap 46kV Line (~4 miles included in total length above) Guthrie Tap 46kV Line serves 22 MVA of peak load served radially Line conductor is 1964 vintage 4/0 ACSR.