## Sheet1
Region | Upgrade ID | Description | Transmisison Owner | Required In Service Date | Revised Required In Service Date | Status | TEAC Cost | TEAC Date | Latest TEAC Date | Database Notes | Board Date | Initial Issue Assessment | Final Assessment
PJM WEST | b3104 | Perform a sag study on the Polaris - Westerville 138 kV line (~ 3.6 miles) to increase the Summer Emergency rating to 310 MVA. | AEP | 2020-06-01 |  | EP | 3.82 | 2019-03-07 | 2022-10-04 | Conesville 4 | 2019-07-29 | Scope/Cost Change | Scope/Cost Change
PJM MA | b3719 | Replace the two existing 1200A Bergen 138kV Circuit Switchers with two (2) 138kV Disconnect Switches to achieve a minimum summer normal device rating of 298 MVA and a minimum summer emergency rating of 454 MVA | PSEG | 2022-12-31 |  | PL | 1.2 | 2022-09-15 | 2022-09-15 | Immediate Need (Baseline Load Growth Deliverability & Reliability) |  | New Upgrade | New Upgrade
PJM WEST | b3720 | Rebuild the Abbe-Johnson #2 69 kV Line (approx. 4.9 miles) with 556 kcmil ACSR conductor. Replace (3) disconnect switches (A17, D15 & D16) and line drops and revise relay settings at Abbe. Replace (1) disconnect switch (A159) and line drops and revise relay settings at Johnson. Replace (2) MOAB disconnect switches (A4 & A5), (1) disconnect switch (D9), and line drops at Redman. | ATSI | 2027-06-01 |  | PL | 10.9 | 2022-10-14 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3721 | Rebuild and reconductor the Avery-Hayes 138 kV line (approx. 6.5 miles) with 795 KCMIL 26/7 ACSR | ATSI | 2027-06-01 |  | PL | 10.4 | 2022-10-14 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3722 | Rebuild the existing Darrah - Barnett 69 kV line, approximately 2.8 miles and replace a riser at Darrah Station. | AEP | 2027-12-01 |  | PL | 6.98 | 2022-10-14 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3723 | Rebuild the George Washington – Kammer 138kV circuit, except for 0.1-mile of previously-upgraded T-line outside each terminal station (6.7 miles of total upgrade scope). Remove the existing 6-wired steel lattice towers and supplement the right-of-way as needed. | AEP | 2027-06-01 |  | PL | 18.3 | 2022-10-14 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3724 | Install 138 kV circuit switcher on the high-side of Transformer #2 at Roanoke Station (previously proposed as a portion of s2469.7, posted in 2021 AEP local plan) . | AEP | 2027-06-01 |  | PL | 0.1 | 2022-10-14 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3725 | Replace the 1600A bus disconnect switch at Goodings Grove on L11622 Elwood-Goodings Grove 345 kV. | ComEd | 2027-12-01 |  | PL | 0.5 | 2022-10-04 |  |  |  | New Upgrade | New Upgrade