## Current List
Region | Upgrade ID | Description | Transmisison Owner | Required In Service Date | Revised Required In Service Date | Status | TEAC Cost | TEAC Date | Latest TEAC Date | Database Notes | Board Date | Initial Issue Assessment | Final Assessment
PJM WEST | b3710 | Expand the future AA2-161 138 kV six (6) breaker ring bus into an eleven (11) breaker substation with a breaker-and-a-half layout by constructing five (5) additional breakers and expanding the bus. Loop the Yukon - Charleroi #2 138 kV line into the future AA2-161 substation. Relocate terminals as necessary at AA2-161. Upgrade terminal equipment (wavetrap, substation conductor) and relays at Yukon, Huntingdon, Springdale, Charleroi, and the AA2-161 substation. | APS | 2026-06-01 |  | PL | 10.64 | 2022-04-22 | 2022-11-18 |  |  | New Upgrade | Scope/Cost Change
PJM WEST | b3731 | Replace 40kV breaker J at McComb station with a new 3000A 40kA breaker | AEP | 2027-06-01 |  | PL | 0.5 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3732 | Install a 6 MVAR, 34.5kV cap bank at Morgan Run station | AEP | 2027-06-01 |  | PL | 0.37 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3733 | Rebuild the 1.8 mile 69kV T-line between Summerhill and Willow Grove Switch. Replace 4/0 ACSR conductor with 556 ACSR. | AEP | 2027-06-01 |  | PL | 5.1 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3734 | Install a 7.7 MVAR, 69kV cap bank at both Otway station and Rosemount station | AEP | 2027-06-01 |  | PL | 1.73 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3735 | Terminate the existing Broadford – Wolf Hills #1 138 kV line into Abingdon 138 kV Station. This line currently bypasses the existing Abingdon 138 kV Station; Install two new 138 kV circuit breakers on each new line exit towards Broadford and towards Wolf Hills #1; Install one new 138 kV circuit breaker on line exit towards South Abingdon for standard bus sectionalizing | AEP | 2027-06-01 |  | PL | 8.48 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.1 | Establish 69kV bus and new 69 kV line CB at Dorton substation. | AEP | 2027-12-01 |  | PL | 1.13 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.10 | Henry Clay S.S Retirement: | AEP | 2027-12-01 |  | PL | 0.3 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.11 | Cedar Creek substation work | AEP | 2027-12-01 |  | PL | 0.44 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.12 | Breaks substation retire 46kV equipment: | AEP | 2027-12-01 |  | PL | 0.25 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.13 | Retire Pike 29 SS and Rob Fork SS | AEP | 2027-12-01 |  | PL | 0.42 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.14 | Serve Pike 29 and Rob Fork customers from nearby 34kV Distribution sources. | AEP | 2027-12-01 |  | PL | 0 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.15 | Poor Bottom substation install | AEP | 2027-12-01 |  | PL | 0 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.16 | Henry Clay 46kV substation retirement | AEP | 2027-12-01 |  | PL | 0 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.17 | New Draffin 69kV substation install | AEP | 2027-12-01 |  | PL | 0 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.18 | Draffin 46kV substation retirement | AEP | 2027-12-01 |  | PL | 0 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.2 | At Breaks substation, reuse 72kV breaker A as the new 69kV line breaker. | AEP | 2027-12-01 |  | PL | 0.71 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.3 | Rebuild ~16.7 mi Dorton – Breaks 46kV line to 69kV | AEP | 2027-12-01 |  | PL | 58.52 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.4 | Retire ~17.2 mi Cedar Creek – Elwood 46kV circuit. | AEP | 2027-12-01 |  | PL | 11.15 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.5 | Retire ~ 6.2 mi Henry Clay – Elwood 46kV line section. | AEP | 2027-12-01 |  | PL | 4.3 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.6 | Retire Henry Clay 46 kV substation and replace with Poor Bottom 69 kV station. Install a new 0.7 mi double circuit extension to Poor Bottom 69kV. | AEP | 2027-12-01 |  | PL | 3.42 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.7 | Retire Draffin substation and replace with a new substation. Install a new 0.25 mi double circuit extension to New Draffin substation. | AEP | 2027-12-01 |  | PL | 2.01 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.8 | Remote End work at Jenkins substation | AEP | 2027-12-01 |  | PL | 0.03 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3736.9 | Provide Transition fiber to Dorton, Breaks, Poor Bottom, Jenkins and New Draffin substations | AEP | 2027-12-01 |  | PL | 0.41 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3738 | Charleroi - Dry Run 138 kV Line: Replace Limiting Terminal Equipment | AP | 2027-06-01 |  | PL | 0.38 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3739 | Dry Run - Mitchell 138 kV Line: Replace Limiting Terminal Equipment | AP | 2027-06-01 |  | PL | 0.4 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3740 | Glen Falls - Bridgeport 138 kV Line: Replace Limiting Terminal Equipment | AP | 2027-06-01 |  | PL | 1.88 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3741 | Yukon - Charleroi No.1 138 kV Line: Replace Limiting Terminal Equipment | AP | 2027-06-01 |  | PL | 0.7 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3742 | Yukon - Charleroi No.2 138 kV Line: Replace Limiting Terminal Equipment | AP | 2027-06-01 |  | PL | 0.45 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3743 | At Bedington Substation: Replace substation conductor, wavetrap, CT's and upgrade relaying At Cherry Run Substation: Replace substation conductor, wavetrap, CT's, disconnect switches, circuit breaker and upgrade relaying At Marlowe: Replace substation conductor, wavetrap, CT's and upgrade relaying. | AP | 2027-06-01 |  | PL | 4.6 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3744 | Replace one span of 1272 ACSR from Krendale substation to structure 35 (~630 ft) Replace one span of 1272 ACSR from Shanor Manor to structure 21 (~148 ft) Replace 1272 ACSR risers at Krendale & Shanor Manor Substations Replace 1272 ACSR Substation Conductor at Krendale Substation Replace relaying at Krendale Substation Revise Relay Settings at Butler & Shanor Manor Substations. | AP | 2027-06-01 |  | PL | 1.75 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3745 | Carbon Center Substation - Install Redundant Relaying | AP | 2027-06-01 |  | PL | 0.57 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3746 | Meadow Brook Substation - Install Redundant Relaying | AP | 2027-06-01 |  | PL | 0.21 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3747 | Bedington Substation - Install Redundant Relaying | AP | 2027-06-01 |  | PL | 0.28 | 2022-11-18 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3749 | Rebuild the New Church - Piney Grove 138 kV line | DPL | 2027-06-01 |  | PL | 63 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM MA | b3750 | Upgrade Seward Terminal Equipment of the Seward-Blairsville 115 kV Line to increase the line rating such that the Transmission Line conductor is the limiting component. | PENELEC | 2027-06-01 |  | PL | 0.43 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM MA | b3751 | Rebuild 6.4 miles of the Roxbury - Shade Gap 115 kV line from Roxbury to the AE1-071 115 kV ring bus with single circuit 115 kV construction | PENELEC | 2027-06-01 |  | PL | 15.03 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM MA | b3752 | Rebuild 7.2 miles of the Shade Gap - AE1-071 115 kV line section of the Roxbury - Shade Gap 115 kV line | PENELEC | 2027-06-01 |  | PL | 17.43 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM MA | b3753 | Replace the Tyrone North 115 /46 kV transformer with a new standard 75 MVA top rated bank and upgrade the entire terminal to minimum 100 MVA capability for both SN and SE rating | PENELEC | 2027-06-01 |  | PL | 2.82 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM MA | b3754 | At Maclane tap: Construct a new three breaker ring bus to tie into the Warrior Ridge - Belleville 46 kV D line and the 1LK line | PENELEC | 2027-06-01 |  | PL | 10.09 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM MA | b3755 | Convert Locust Street 69kV from a Straight Bus to a Ring Bus. | PSEG | 2027-06-01 |  | PL | 30 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM MA | b3756 | Convert Maple Shade 69kV from a Straight Bus to a Ring Bus | PSEG | 2027-06-01 |  | PL | 33.9 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM MA | b3758 | Construct a new 69kV line from 14th Street to Harts Lane | PSEG | 2027-06-01 |  | PL | 34.4 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM SOUTH | b3759 | Reconductor approximately 10.5 miles of 115kV Line #23 segment from Oak Ridge to AC2-079 Tap to minimum emergency ratings of 393 MVA Summer / 412 MVA Winter | Dominion | 2027-06-01 |  | PL | 23.5 | 2022-10-13 | 2022-11-17 |  |  | New Upgrade | New Upgrade
PJM WEST | b3761 | Install 138 kV Breaker on the Ridgway 138/46 kV #2 Transformer | AP | 2027-06-01 |  | PL | 1.1 | 2022-12-16 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3762 | Rebuild EKPC’s Fawkes-Duncannon Lane Tap 556.5 ACSR 69 kV line section (7.2 miles) using 795 ACSR. | EKPC | 2026-12-01 |  | PL | 8.5 | 2022-12-16 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3763 | Replace the Jug Street 138kV breakers M, N, BC, BF, BD, BE, D, H, J, L, BG, BH, BJ, BK with 80KA breakers | AEP | 2024-06-01 |  | PL | 14 | 2022-12-16 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3764 | Replace the Hyatt 138kV breakers AB1 and AD1 with 63kA breakers | AEP | 2024-06-01 |  | PL | 2 | 2022-12-16 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3765 | Purchase one 80 MVAR 345 kV spare reactor, to be located at the Mainesburg station. | PENELEC | 2022-12-01 |  | PL | 6.44 | 2022-11-04 | 2022-12-06 |  |  | New Upgrade | New Upgrade
PJM MA | b3768 | Rebuild/Reconductor the Germantown - Lincoln 115 kV Line. Approximately 7.6 miles. Upgrade limiting terminal equipment at Lincoln, Germantown and Straban | ME | 2027-06-01 |  | PL | 17.36 | 2022-12-06 | 2023-01-06 |  |  | New Upgrade | New Upgrade
PJM MA | b3769 | Install second TMI 500/230kV Transformer with additional 500 and 230 bus expansions | ME | 2027-06-01 |  | PL | 30.19 | 2022-12-06 | 2023-01-06 |  |  | New Upgrade | New Upgrade
PJM MA | b3770 | Rebuild 1.4 miles of existing single circuit 230 kV tower line between BGE's Graceton substation to the Brunner Island PPL tie-line at the MD/PA state line to double circuit steel pole line with one (1) circuit installed to uprate 2303 circuit | BGE | 2027-06-01 |  | PL | 8.4 | 2022-12-06 | 2023-01-06 |  |  | New Upgrade | New Upgrade
PJM MA | b3771 | Reconductor two (2) 230 kV circuits from Conastone to Northwest #2 | BGE | 2027-06-01 |  | PL | 37.76 | 2022-12-06 | 2023-01-06 |  |  | New Upgrade | New Upgrade
PJM SOUTH | b3772 | Reconductor 27.3 miles of the Messick Road - Morgan 138 kV Line from 556 ACSR to 954 ACSR. At Messick Road Substation: Replace 138 kV wave trap, circuit breaker, CT's, disconnect switch, and substation conductor and upgrade relaying. At Morgan Substation: Upgrade Relaying | APS | 2027-06-01 |  | PL | 49.23 | 2022-12-06 | 2023-01-06 |  |  | New Upgrade | New Upgrade
PJM WEST | b3773 | McConnellsburg 138 kV Susbtation: Install 33 MVAR switched capacitor, 138 kV Breaker, and associated relaying | APS | 2027-06-01 |  | PL | 3.05 | 2022-12-06 | 2023-01-06 |  |  | New Upgrade | New Upgrade
PJM MA | b3774 | Upgrade terminal equipment at Brunner Island (on the Brunner Island - Yorkana 230 kV circuit) | PPL | 2027-06-01 |  | PL | 2.5 | 2022-12-06 | 2023-01-06 |  |  | New Upgrade | New Upgrade
PJM WEST | b3775.1 | Outside of the Green Acres substation, swap the NIPSCO Green Acre Tap towers from the St. John-Green Acres-Olive 345 kV line to the University Park N-Olive 345 kV line to create a University Park N-Green Acres-Olive and St. John-Olive 345 kV lines. | NEET | 2026-12-01 |  | PL | 1.98 | 2023-01-10 |  | 2022_MD-644 (modified) |  | New Upgrade | New Upgrade
PJM WEST | b3775.10 | Perform a sag study on the Olive – University Park 345kV line to increase the operating temperature to 225 F. Remediation work includes two tower replacements on the line. | AEP | 2026-12-01 |  | PL | 1.5 | 2023-01-10 |  | 2022_MD-908 |  | New Upgrade | New Upgrade
PJM WEST | b3775.2 | Reconductor NEET’s section of Crete(IN/IL border)-St. John 345 kV line (6.95 miles). | NEET | 2026-12-01 |  | PL | 1.99 | 2023-01-10 |  | 2022_MD-644 (modified) |  | New Upgrade | New Upgrade
PJM WEST | b3775.3 | Rebuild ComEd’s section of 345 kV double circuit in IL from St. John to Crete (5 miles) with twin bundled 1277 ACAR conductor. | ComEd | 2026-12-01 |  | PL | 16.64 | 2023-01-10 |  | 2022_MD-253 |  | New Upgrade | New Upgrade
PJM WEST | b3775.4 | Rebuild 12.7 miles of 345 kV double circuit extending from Crete to E. Frankfort with twin bundled 1277 ACAR conductor. | ComEd | 2026-12-01 |  | PL | 42.28 | 2023-01-10 |  | 2022_MD-253 |  | New Upgrade | New Upgrade
PJM WEST | b3775.5 | Replace E. Frankfort 345 kV circuit breaker “9-14” with 3150A SF6 circuit breaker. | ComEd | 2026-12-01 |  | PL | 3.27 | 2023-01-10 |  | 2022_MD-253 |  | New Upgrade | New Upgrade
PJM WEST | b3775.6 | Perform sag study mitigation work on the Dumont-Stillwell 345 kV line (remove a center-pivot irrigation system from under the line, allowing for the normal and emergency ratings of the line to increase) | AEP | 2026-12-01 |  | PL | 0.22 | 2023-01-10 |  | 2022_MD-644 (modified) |  | New Upgrade | New Upgrade
PJM WEST | b3775.7 | Upgrade the limiting element at Stillwell or Dumont substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | AEP | 2026-12-01 |  | PL | 2 | 2023-01-10 |  | 2022_MD-644 (modified) |  | New Upgrade | New Upgrade
PJM WEST | b3775.8 | Upgrade the existing terminal equipment (substation conductor) at St. John on the existing Crete to St. John 345 kV line with bundled 2x1590 ACSR Lapwing | NIPSCO | 2026-12-01 |  | PL | 2 | 2023-01-10 |  | 2022_MD-644 (modified) |  | New Upgrade | New Upgrade
PJM WEST | b3775.9 | Upgrade the existing terminal equipment (substation conductor) at Green Acres on the existing St. John to Green Acres 345 kV line with bundled 2x1590 ACSR Lapwing | NIPSCO | 2026-12-01 |  | PL | 2 | 2023-01-10 |  | 2022_MD-644 (modified) |  | New Upgrade | New Upgrade
PJM WEST | b3317 | Modify backup relay clearing times at the 138 kV STA16 Waukegan station. | ComEd | 2023-06-01 |  | EP | 0.255 | 2021-05-21 |  |  | 2005-05-09 | Cancelled in Database | Cancelled
Formulas:
Board Date = IF(COUNTIF([1]!B_DB_Board[Upgrade ID],[1]!B_History[[#This Row],[Upgrade ID]])=1,LOOKUP([1]!B_History[[#This Row],[Upgrade ID]],[1]!B_DB_Board[Upgrade ID],[1]!B_DB_Board[Board Approval Date]),"")