## Sheet1
Region | Upgrade ID | Description | Transmisison Owner | Required In Service Date | Revised Required In Service Date | Status | TEAC Cost | TEAC Date | Latest TEAC Date | Notes | Board Date | Initial Issue Assessment | Final Assessment
PJM SOUTH | b3694.8 | Partial wreck and rebuild 10.34 miles of 230 kV line #249 Carson-Locks to achieve a minimum summer emergency rating of 1047 MVA. Upgrade terminal equipment at Carson and Locks to not limit the new conductor rating. | Dominion | 2026-06-01 |  | EP | 25.6 | 2021-11-30 | 2024-01-09 | Proposal #2021_1-224 | 2022-02-16 | Scope/Cost Change | Scope/Cost Change
PJM MA | b3737.22 | Construct the Larrabee Collector station AC switchyard, composed of a 230 kV 3 x breaker and a half substation with a nominal current rating of 4000 A and four single phase 500/230 kV 450 MVA autotransformers to step up the voltage for connection to the Smithburg substation. Procure land adjacent to the AC switchyard, and prepare the site for construction of future AC to DC converters for future interconnection of DC circuits from offshore wind generation. Land should be suitable to accommodate installation of four individual converters to accommodate circuits with equivalent rating of 1400 MVA at 400 kV. | MAOD | 2027-12-31 |  | PL | 216.3 | 2022-11-04 | 2024-01-09 | 2021_SAA-550 | 2022-12-06 | Scope/Cost Change | Scope/Cost Change
PJM MA | b3780.14 | Reconfigure Cooper transmission feeds by establishing new Cooper - North Delta 230kV line and rerouting existing transmissions lines by Cooper | PECO | 2025-06-01 |  | PL | 3.6 | 2023-12-05 | 2024-01-09 |  |  | Scope/Cost Change | New Upgrade
PJM MA | b3780.15 | Cut-in 5012 Peach Bottom - Conastone 500kV line into North Delta 500/230kV substation by rebuilding 5012 between new terminal at Peach Bottom South and North Delta on single circuit structures and terminating at North Delta | PECO | 2025-06-01 |  | PL | 7.86 | 2023-12-05 | 2024-01-09 |  |  | Scope/Cost Change | New Upgrade
PJM MA | b3780.16 | North Delta 230 kV termination for new Cooper - North Delta 230 kV line (Transource Scope) | Transource | 2025-06-01 |  | PL | 0.47 | 2023-12-05 | 2024-01-09 |  |  | Scope/Cost Change | New Upgrade
PJM MA | b3780.17 | Cut-in 5012 Peach Bottom - Conastone 500kV line into North Delta 500/230kV substation by rebuilding 5012 between new terminal at Peach Bottom South and North Delta on single circuit structures and terminating at North Delta (Transource Scope) | Transource | 2025-06-01 |  | PL | 1.1 | 2023-12-05 | 2024-01-09 |  |  | Scope/Cost Change | New Upgrade
PJM WEST | b3784.1 | Replace 138kV breaker 5 at Canal St station with a new 3000A 63kA breaker | AEP | 2028-06-01 |  | PL | 0.5 |  |  | Immediate Need (Short Circuit) |  | New Upgrade | New Upgrade
PJM WEST | b3785.1 | Replace existing 3000 A wavetrap at Mountaineer 765 kV, on the Belmont - Mountaineer 765 kV line, with a new 5000 A wavetrap. | AEP | 2028-06-01 |  | PL | 0.46 | 2023-12-05 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3786.1 | Rebuild ~4.5 miles of 69 kV line between Abert and Reusens Substations. Update Line Settings at Reusens and Skimmer. | AEP | 2028-06-01 |  | PL | 14.4023 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3787.1 | Install a CCVT on 3 phase stand and remove the single phase existing CCVT on the 69kV Coalton to Bellefonte line exit. The existing CCVT is mounted to lattice on a single phase CCVT stand, which will be replaced with the 3 phase CCVT stand. The line riser between line disconnect and line take off is being replaced. This remote end work changes the MLSE of the line section between Coalton - Princess 69kV line section. | AEP | 2028-12-01 |  | PL | 0 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3788.1 | Replace AEP owned station takeoff riser and breaker BB risers at OVEC owned Kyger Creek station. | AEP | 2028-06-01 |  | PL | 0.41 | 2023-12-05 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3788.2 | Replace OVEC owned breaker AA risers, bus work, and breaker AA disconnect switches at OVEC owned Kyger Creek station. | OVEC | 2028-06-01 |  | PL | 0.75 | 2023-12-05 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3789 | A 69 kV, 60 MVAR Shunt Reactor will be installed at the Salt Springs Substation. The reactor terminal will be connected to the existing 69 kV bus and an independent-pole operation, 1200 A circuit breaker will be installed for reactor switching. | ATSI | 2028-06-01 |  | PL | 5.45 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3790 | Olive 345kV Breaker “D” Replacement Replace the overdutied Olive 345kV circuit breaker "D" with a 5000A 63 kA circuit breaker. Re-use existing cables and a splice box to support the CB install. | AEP |  |  | PL | 1.083 | 2023-12-05 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3791 | Rebuild the North Meshoppen - Mehoopany #1 115 kV Line with 795 ACSR 26/7 STR conductor. Upgrade terminal equipment to exceed transmission line ratings. | PENELEC | 2028-06-01 |  | PL | 17.4 | 2023-10-19 | 2023-11-16 |  |  | New Upgrade | New Upgrade
PJM MA | b3792 | Rebuild the North Meshoppen - Mehoopany #2 115 kV Line using 795 ACSR 26/7 STR conductor and upgrade terminal equipment to exceed the transmission line rating | PENELEC | 2028-06-01 |  | PL | 17.7 | 2023-10-19 | 2023-11-16 |  |  | New Upgrade | New Upgrade
PJM MA | b3793.1 | Reconductor Silver Run - Cedar Creek 230kV line. Reconductor 8.8 miles of 230 kV Circuit with 1594-T11/ACCR “Lapwing” conductor and replace all insulators with high temp hardware | DPL | 2028-06-01 |  | PL | 7.68 | 2023-10-31 | 2023-12-05 |  |  | New Upgrade | New Upgrade
PJM MA | b3793.2 | Cedar Creek – Replace three (3) standalone CTs, disconnect switch, stranded bus, and rigid bus to achieve higher rating | DPL | 2028-06-01 |  | PL | 0.453 | 2023-10-31 | 2023-12-05 |  |  | New Upgrade | New Upgrade
PJM MA | b3793.3 | Silver Run - Replace three(3) 1-1590 ACSR Jumpers and one(1) air disconnect switch | DPL | 2028-06-01 |  | PL | 0.58 | 2023-10-31 | 2023-12-05 |  |  | New Upgrade | New Upgrade
PJM MA | b3794.1 | Replace existing Waldwick 230kV 50MVAR fixed shunt reactor with a 230kV 150MVAR variable shunt reactor | PSEG | 2028-06-01 |  | PL | 13.6 | 2023-10-31 | 2023-12-05 |  |  | New Upgrade | New Upgrade
PJM MA | b3794.2 | Replace existing Waldwick 345kV 100MVAR fixed shunt reactor with a 345kV 150MVAR variable shunt reactor | PSEG | 2028-06-01 |  | PL | 16 | 2023-10-31 | 2023-12-05 |  |  | New Upgrade | New Upgrade
PJM WEST | b3796 | Replace the Belmont 765/500 kV Transformer #5 with a new transformer bank consisting of three single-phase transformers and an additional single phase spare transformer. | APS | 2028-06-01 |  | PL | 42.05 | 2024-01-09 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3800.2 | Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV Switchyard. | ME | 2027-06-01 |  | EP | 18.3 | 2023-12-05 | 2024-01-09 | 2022-W3-374 | 2023-12-11 | Scope/Cost Change | Scope/Cost Change
PJM MA | b3800.45 | North Delta 500 kV termination for the Rock Springs 500 kV line (5034/5014 line) (PECO work). | PECO | 2027-06-01 |  | UC | 0.8 | 2023-10-31 | 2024-01-09 | 2022-W3-344 | 2023-12-11 | Scope/Cost Change | Scope/Cost Change
PJM MA | b3800.52 | Reconfigure Peach Bottom North and South yards to allow for termination of 500kV lines from Peach Bottom to North Delta.North Delta 500 kV termination for the new Peach Bottom - North Delta 500 kV line | PECO | 2027-06-01 |  | PL | 7.86 | 2023-10-31 | 2024-01-09 |  |  | Scope/Cost Change | New Upgrade
PJM WEST | b3810 | Add three 345 kV circuit breakers to Cherry Valley substation. | ComEd | 2028-06-01 |  | PL | 7.75 | 2024-01-09 |  | 2023-W1-771 |  | New Upgrade | New Upgrade
PJM WEST | b3836.1 | Rebuild approximately 1.7 miles of line on the Chemical - Washington Street 46 kV circuit | AEP | 2028-06-01 |  | PL | 7.6 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3837.1 | Replace existing 34.5 kV, 25 kA circuit breaker B at West Huntington Station with new 69 kV, 40 kA circuit breaker | AEP | 2028-06-01 |  | PL | 0.3648 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3838.1 | Replace breaker A and B at Timken Station with 40 kA breakers | AEP | 2028-06-01 |  | PL | 1.2 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3839.1 | Replace 69kV breaker C at Haviland station with a new 3000A 40kA breaker | AEP | 2028-06-01 |  | PL | 0.4 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3840.1 | Replace Structures 382-66 and 382-63 on Darrah - East Huntington 34.5 kV line to bypass 24th Street station. Retire structures 1 through 5 on Twenty Fourth Street 34.5 kV Extension. Retire 24th Street Station. Remove conductors from BASF Tap to BASF. | AEP | 2028-06-01 |  | PL | 1.8 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3843.1 | Rebuild the underground portion of the Ohio University-West Clark 69 kV line, approximately 0.65 miles. | AEP | 2028-06-01 |  | PL | 4.6 | 2023-11-17 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3844.1 | Replacement of relays at Macdade, Printz, and Morton to increase rating limits of transmission relay equipment. Line protection relays will be upgraded with latest standard relays used across the PECO system. | PECO | 2026-12-31 |  | PL | 1.3998 | 2023-12-05 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3845.1 | Add a second breaker next to Nottingham 895 CB to eliminate stuck breaker contingency. | DPL | 2028-05-31 |  | PL | 1.2844 | 2023-11-16 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3846.1 | Rebuild 6.25 miles of 69kV circuit 6708 (Vienna – Mardela) with new single pole steel structures and with 954.0 45/7 "Rail" conductor. This new rebuild will be from the dead-end structure on the east side of the Nanticoke River to the Mardela Tap. | DPL | 2028-05-31 |  | PL | 18.6294 | 2023-11-16 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3846.2 | Upgrade of disconnect switch at Vienna to increase ratings of existing Vienna - Mardela transmission facility. | DPL | 2028-05-31 |  | PL | 1 | 2023-11-16 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3846.3 | Upgrade of three disconnect switches at Mardela to increase ratings of existing Vienna - Mardela transmission facility. | DPL | 2028-05-31 |  | PL | 1.75 | 2023-11-16 |  |  |  | New Upgrade | New Upgrade