## 500 kV
500 KV OH DESIGN STANDARDS
Criteria Items | NESC 2012 | PJM 2002 TSDS Guidelines
ENVIRONMENTAL/GENERAL
Ambient Temperature Range | N/A | -30ᴼC to +40ᴼC (from -40ᴼC N & W of Blue Mountain)
Keraunic Level | N/A | 40
Minimum Extreme Wind Loading | NESC 250C WIND MAP | 25 psf
Heavy Ice Load (No Wind) | 1" | 1 1/2"
Code Requirements | NESC Grade "B" Heavy | NESC Grade "B" Heavy
Provisions for Live Line Maintenance | NESC Rule 441 | As required by the TO
Access Requirements | Not Specified | Construction and maintenance access is required to each structure
Line crossings | Not Specified | NESC clearance for tranmission line crossing 10' minimum for lines 230 kV and below
Line cascade mitigation | Not Specified | Dean End Strain every 5 mile
Structure Finish | Not Specified | By TO
ELECTRICAL
RIV Level @ 350 kV line to ground | Not Specified | 300uV @ 1MHz
Switching Surge Factor | Not Specified | 2.2 P.U.
1.2 x 50 µs minimum critical flashover | Not Specified | 2145 kV
Lightning Trip out Performance (line) | Not Specified | 1/100 miles (160km) per year
Line trip out performance from all other causes | Not Specified | 1/100 miles (160km) per year
Sag and tension Calculation method | Not Specified | Alcoa Sag & Tension Software or equivalent
Galloping Mitigation | Not Specified | Provide adequate clearance so that 12" of clearance exists between wire galloping ellipses to minimize conductor or structure damage. The TO may revise this requirement for areas with significant galloping history.
Damper Requirements | Intial unloaded tension 35% Final unloaded tension 25% | <18% RBS (No dampers required) 18%-20% RBS (Dampers required)
Spacers | Not Specified | 18" spacing - NO preformed wire spacers allowed
Approved conductor sizes for NEW construction | Not Specified | Match approved conductor sizes and bundle configuration with local utility company
Approved static and OPGW wires sizes for NEW construction | Not Specified | Match approved conductor sizes with the TO
Ratings of conductors | Not Specified | PJM TSDS Bare Overhead Transmission Conductor Ratings, November 2000
Conductor Operation Temperature and Conductor Sag | Not Specified
Min Conductor Operating Temp for Sagging and Clearance Purposes | Not Specified | ACAR - 100ᴼC ACSR, ACSS - 125ᴼC
Maximum Operating Temperature | Not Specified | ACAR - 140ᴼC ACSR, ACSS - 180ᴼC
Right-Of-Way width (Target values) | Not Specified | 200 Ft - 1 CKT 300 Ft. (min) - 2 ckts
Max. Number of circuits per structure | Not Specified | 1 unless specifically approved by TO
Min. design ground clearance at Max. sag | NESC Rule 232 | NESC minimum requirements PLUS an additional 3 feet
Conductor to structure steel clearance (min.) | NESC Rule 235 | 125 in all anticipated conductor positions from an every day condition to a displaced conductor due to 9 psf wind or ice loading, based on 2.2 per unit switching surge values
Wire-to-wire clearances | NESC Rule 233 | Min. NESC Rule 233 and 235. 20 ft. min for lower non-transmission wire, trans wire calculated at max operating temp or heavy ice, whichever great sag and non-transmission wire at 0ᴼF
Clearances between transmission conductors | NESC Rule 233 | Larger of either 2.2 per unit switching surge or clearances based on NESC
Conductor Tension Limits
NESC 250B | 60% | Not Specified
NESC 250C | 80% | Not Specified
NESC 250D | 80% | Not Specified
Heavy Ice
No Wind, No Ice, 60ᴼF, Initial | 35% | Not Specified
No Wind, No Ice, 60ᴼF, Final | 25% | 18-20%
Insulation Requirements
Leakage Distance | Not Specified | 360 in
60 Hz Wet | Not Specified | 950 kV
Switching Surge | Not Specified | 2.2 per unit
Critical Impulse Flashover | Not Specified | 2145 kV
Maximum Structure Ground Resistance | Not Specified | 15 ohms. Individual tower ground measurements will be allowed to exceed if the avg value for the 5 adjacent structures along line is less than the 15 ohms
Step & Touch Potential Issues | Not Specified | Provide a structure grounding system that meets the step and touch requirements of the TO
Minimum Number of Static Wires Required | Not Specified | Minimum of 1 per circuit
Maximum Shielding Angle | Not Specified | 15ᴼ
EMF Limits | Not Specified | As Required by TO and State Regulatory Agencies EPRI ENVIRO or equiv software
Radio Interference at edge of right-of-way | Not Specified | 300µV @ 1MHZ (350 kV to gnd) Perform investigation to measure actual radio and TV signal strength and calculate the signal to noise ratio
Audible Noise | Not Specified | Per applicable state laws for noise at edge of right-of-way Using wet conductor design condition
Voltage gradient | Not Specified | Not specified
Inductive interference | Not Specified | Not specified
Line transpositions | Not Specified | Not specified
STRUCTURAL
S1. Steel Structure Design Loading Conditions
a. NESC Heavy Loading District
Wind Pressure on wires (psf) | 4 | 4
Wind Pressure on structure (psf) | 4 | 4
Radial Ice (inches) | 0.5 | 0.5
Temperature (deg F) | 0 | 0
Load Constant (lbs) | 0.3 | 0.3
Load Factors | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65 | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65
b. NESC 250C Extreme Wind
Wind Pressure on wires (psf) | NESC 250C Wind Map | 25
Wind Pressure on structure (psf) | NESC 250C Wind Map | 31.25
Radial Ice (inches) | N/A | 0
Temperature (deg F) | 60 | 60
Load Constant (lbs) | N/A | N/A
Load Factors | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00 | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
c. NESC 250D Concurrent Wind & Ice
Wind Pressure (psf) | NESC 250D Wind and Ice Map | Not specified
Wind Pressure on structure (psf) | NESC 250D Wind and Ice Map | Not specified
Radial Ice (inches) | NESC 250D Wind and Ice Map | Not specified
Temperature (deg F) | NESC Table 250 | Not specified
Load Constant (lbs) | N/A | Not specified
Load Factors | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00 | Not specified
d. Heavy Ice
Wind Pressure (psf) | N/A | 0
Wind Pressure on structure (psf) | N/A | 0
Radial Ice (inches) | N/A | 1.5
Temperature (deg F) | N/A | 32
Load Constant (lbs) | N/A | N/A
Load Factors | Wind: N/A Vertical: N/A Tension: N/A | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
e. Longitudinal for Suspension
d.1. One broken conductor or static wire
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.10 Transverse: 1.10 Vertical: 1.10 Tension: 1.10
d.2. Differential ice loading
Wind Pressure (psf) | Not Specified | 0
Wind Pressure on structure (psf) | Not Specified | 0
Radial Ice (inches) | Not Specified | 1.0" one side/0" other side
Temperature (deg F) | Not Specified | 32
Load Constant (lbs) |  | N/A
Load Factors | Not Specified | Wind: 1.10 Wind on structure: 1.10 Vertical: 1.10 Tension: 1.10
d.3. Bound stringing block
Wind Pressure (psf) | Not Specified | 2
Wind Pressure on structure (psf) | Not Specified | 4
Radial Ice (inches) | Not Specified | 0
Temperature (deg F) | Not Specified | 30
Load Constant (lbs) | Not Specified | N/A
Load Factors | Not Specified | Wind: 2.0 Transverse: 2.0 Vertical: 2.0 Tension: 2.0
f. Longitudinal for Strain
f.1. One broken conductor or static wire
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.10 Transverse: 1.10 Vertical: 1.10 Tension: 1.10
f.2. All conductors and static wires broken
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
g. Longitudinal for Dead End
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65
h. Longitudinal for Line Termination | Not Specified | Same as Intact Conditions
CIVIL/FOUNDATIONS
Flood Plain | Not Specified | Meet applicable local, State and Federal Regulations
A. Drilled Pier (Caisson)
Design | Not Specified | Not specified
Foundation Diameter | Not Specified | Not specified
Foundation Reveal | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | 1.25 times the design factored load reactions for overturning moment and uplift foundations and 1.10 times the design factored loads for the compression foundations
Performance Criteria | Not Specified | Not specified
Concrete | Not Specified | Not specified
B. Directly Embedded Structure
Design | Not Specified | Not specified
Excavation Diameter | Not Specified | Not specified
Epoxy Coating | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | Not Specified
Performance Criteria | Not Specified | Not specified
Backfill | Not Specified | Not specified
B. Pile Foundation
Design | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | Not Specified
Pile Performance Criteria | Not Specified | Not Specified
Concrete | Not Specified | Not Specified
C. Specialty Foundation
Design | Not Specified | Not Specified

## 345 kV
345 KV OH DESIGN STANDARDS
Criteria Items | NESC 2012 | PJM 2002 TSDS Guidelines
ENVIRONMENTAL/GENERAL
Ambient Temperature Range | N/A | -30ᴼC to +40ᴼC (from -40ᴼC N & W of Blue Mountain)
Keraunic Level | N/A | 40
Minimum Extreme Wind Loading | NESC 250C WIND MAP | 25 psf
Heavy Ice Load (No Wind) | 1" | 1 1/2"
Code Requirements | NESC Grade "B" Heavy | NESC Grade "B" Heavy
Provisions for Live Line Maintenance | NESC Rule 441 | As required by the TO
Access Requirements | Not Specified | Construction and maintenance access is required to each structure
Line crossings | Not Specified | NESC clearance for tranmission line crossing 10' minimum for lines 230 kV and below
Line cascade mitigation | Not Specified | Dean End Strain every 5 mile
Structure Finish | Not Specified | By TO
ELECTRICAL
RIV Level @ 350 kV line to ground | Not Specified | 300uV @ 1MHz
Switching Surge Factor | Not Specified | 2.4 P.U.
1.2 x 50 µs minimum critical flashover | Not Specified | 1440 kV
Lightning Trip out Performance (line) | Not Specified | 1/100 miles (160km) per year
Line trip out performance from all other causes | Not Specified | 1/100 miles (160km) per year
Sag and tension Calculation method | Not Specified | Alcoa Sag & Tension Software or equivalent
Galloping Mitigation | Not Specified | Provide adequate clearance so that 12" of clearance exists between wire galloping ellipses to minimize conductor or structure damage. The TO may revise this requirement for areas with significant galloping history.
Damper Requirements | Intial unloaded tension 35% Final unloaded tension 25% | <18% RBS (No dampers required) 18%-20% RBS (Dampers required)
Spacers | Not Specified | 18" spacing - NO preformed wire spacers allowed
Approved conductor sizes for NEW construction | Not Specified | Match approved conductor sizes and bundle configuration with local utility company
Approved static and OPGW wires sizes for NEW construction | Not Specified | Match approved conductor sizes with the TO
Ratings of conductors | Not Specified | PJM TSDS Bare Overhead Transmission Conductor Ratings, November 2000
Conductor Operation Temperature and Conductor Sag | Not Specified
Min Conductor Operating Temp for Sagging and Clearance Purposes | Not Specified | ACAR - 100ᴼC ACSR, ACSS - 125ᴼC
Maximum Operating Temperature | Not Specified | ACAR - 140ᴼC ACSR, ACSS - 180ᴼC
Right-Of-Way width (Target values) | Not Specified | 170 Ft - 1 CKT
Max. Number of circuits per structure | Not Specified | 1 unless specifically approved by TO
Min. design ground clearance at Max. sag | NESC Rule 232 | NESC minimum requirements PLUS an additional 3 feet
Conductor to structure steel clearance (min.) | NESC Rule 235 | 91 in all anticipated conductor positions from an every day condition to a displaced conductor due to 9 psf wind or ice loading, based on 2.4 per unit switching surge values
Wire-to-wire clearances | NESC Rule 233 | Min. NESC Rule 233 and 235. trans wire calculated at max operating temp or heavy ice, whichever great sag and non-transmission wire at 0ᴼF
Clearances between transmission conductors | NESC Rule 233 | Larger of either 2.4 per unit switching surge or clearances based on NESC
Conductor Tension Limits
NESC 250B | 60% | Not Specified
NESC 250C | 80% | Not Specified
NESC 250D | 80% | Not Specified
Heavy Ice |  | Not Specified
No Wind, No Ice, 60ᴼF, Initial | 35% | Not Specified
No Wind, No Ice, 60ᴼF, Final | 25% | 18-20%
Insulation Requirements
Leakage Distance | Not Specified | 250 in
60 Hz Wet | Not Specified | 635 kV
Switching Surge | Not Specified | 2.4 per unit
Critical Impulse Flashover | Not Specified | 1440 kV
Maximum Structure Ground Resistance | Not Specified | 15 ohms. Individual tower ground measurements will be allowed to exceed if the avg value for the 5 adjacent structures along line is less than the 15 ohms
Step & Touch Potential Issues | Not Specified | Provide a structure grounding system that meets the step and touch requirements of the TO
Minimum Number of Static Wires Required | Not Specified | Minimum of 1 per circuit
Maximum Shielding Angle | Not Specified | 20ᴼ
EMF Limits | Not Specified | As Required by TO and State Regulatory Agencies EPRI ENVIRO or equiv software
Radio Interference at edge of right-of-way | Not Specified | 300µV @ 1MHZ (350 kV to gnd) Perform investigation to measure actual radio and TV signal strength and calculate the signal to noise ratio
Audible Noise | Not Specified | Per applicable state laws for noise at edge of right-of-way Using wet conductor design condition
Voltage gradient | Not Specified | Not specified
Inductive interference | Not Specified | Not specified
Line transpositions | Not Specified | Not specified
STRUCTURAL
S1. Steel Structure Design Loading Conditions
a. NESC Heavy Loading District
Wind Pressure on wires (psf) | 4 | 4
Wind Pressure on structure (psf) | 4 | 4
Radial Ice (inches) | 0.5 | 0.5
Temperature (deg F) | 0 | 0
Load Constant (lbs) | 0.3 | 0.3
Load Factors | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65 | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65
b. NESC 250C Extreme Wind
Wind Pressure on wires (psf) | NESC 250C Wind Map | 25
Wind Pressure on structure (psf) | NESC 250C Wind Map | 31.25
Radial Ice (inches) | N/A | 0
Temperature (deg F) | 60 | 60
Load Constant (lbs) | N/A | N/A
Load Factors | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00 | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
c. NESC 250D Concurrent Wind & Ice
Wind Pressure (psf) | NESC 250D Wind and Ice Map | Not specified
Wind Pressure on structure (psf) | NESC 250D Wind and Ice Map | Not specified
Radial Ice (inches) | NESC 250D Wind and Ice Map | Not specified
Temperature (deg F) | NESC Table 250 | Not specified
Load Constant (lbs) | N/A | Not specified
Load Factors | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00 | Not specified
d. Heavy Ice
Wind Pressure (psf) | N/A | 0
Wind Pressure on structure (psf) | N/A | 0
Radial Ice (inches) | N/A | 1.5
Temperature (deg F) | N/A | 32
Load Constant (lbs) | N/A | N/A
Load Factors | Wind: N/A Vertical: N/A Tension: N/A | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
e. Longitudinal for Suspension
d.1. One broken conductor or static wire
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.10 Transverse: 1.10 Vertical: 1.10 Tension: 1.10
d.2. Differential ice loading
Wind Pressure (psf) | Not Specified | 0
Wind Pressure on structure (psf) | Not Specified | 0
Radial Ice (inches) | Not Specified | 1.0" one side/0" other side
Temperature (deg F) | Not Specified | 32
Load Constant (lbs) |  | N/A
Load Factors | Not Specified | Wind: 1.10 Wind on structure: 1.10 Vertical: 1.10 Tension: 1.10
d.3. Bound stringing block
Wind Pressure (psf) | Not Specified | 2
Wind Pressure on structure (psf) | Not Specified | 4
Radial Ice (inches) | Not Specified | 0
Temperature (deg F) | Not Specified | 30
Load Constant (lbs) | Not Specified | N/A
Load Factors | Not Specified | Wind: 2.0 Transverse: 2.0 Vertical: 2.0 Tension: 2.0
f. Longitudinal for Strain
f.1. One broken conductor or static wire
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.10 Transverse: 1.10 Vertical: 1.10 Tension: 1.10
f.2. All conductors and static wires broken
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
g. Longitudinal for Dead End
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65
h. Longitudinal for Line Termination | Not Specified | Same as Intact Conditions
CIVIL/FOUNDATIONS
Flood Plain | Not Specified | Meet applicable local, State and Federal Regulations
A. Drilled Pier (Caisson)
Design | Not Specified | Not specified
Foundation Diameter | Not Specified | Not specified
Foundation Reveal | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | 1.25 times the design factored load reactions for overturning moment and uplift foundations and 1.10 times the design factored loads for the compression foundations
Performance Criteria | Not Specified | Not specified
Concrete | Not Specified | Not specified
B. Directly Embedded Structure
Design | Not Specified | Not specified
Excavation Diameter | Not Specified | Not specified
Epoxy Coating | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | Not Specified
Performance Criteria | Not Specified | Not specified
Backfill | Not Specified | Not specified
B. Pile Foundation
Design | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | Not Specified
Pile Performance Criteria | Not Specified | Not Specified
Concrete | Not Specified | Not Specified
C. Specialty Foundation
Design | Not Specified | Not Specified

## 230 kV
230 KV OH DESIGN STANDARDS
Criteria Items | NESC 2012 | PJM 2002 TSDS Guidelines
ENVIRONMENTAL/GENERAL
Ambient Temperature Range | N/A | -30ᴼC to +40ᴼC (from -40ᴼC N & W of Blue Mountain)
Keraunic Level | N/A | 40
Minimum Extreme Wind Loading | NESC 250C WIND MAP | 25 psf
Heavy Ice Load (No Wind) | 1" | 1 1/2"
Code Requirements | NESC Grade "B" Heavy | NESC Grade "B" Heavy
Provisions for Live Line Maintenance | NESC Rule 441 | As required by the TO
Access Requirements | Not Specified | Construction and maintenance access is required to each structure
Line crossings | Not Specified | NESC clearance for tranmission line crossing 10' minimum for lines 230 kV and below
Line cascade mitigation | Not Specified | Dean End Strain every 5 mile
Structure Finish | Not Specified | By TO
ELECTRICAL
RIV Level @ 350 kV line to ground | Not Specified | 300uV @ 1MHz
Switching Surge Factor | Not Specified | 2.5 P.U.
1.2 x 50 µs minimum critical flashover | Not Specified | 1105 kV
Lightning Trip out Performance (line) | Not Specified | 2/100 miles (160km) per year
Line trip out performance from all other causes | Not Specified | 2/100 miles (160km) per year
Sag and tension Calculation method | Not Specified | Alcoa Sag & Tension Software or equivalent
Galloping Mitigation | Not Specified | Provide adequate clearance so that 12" of clearance exists between wire galloping ellipses to minimize conductor or structure damage. The TO may revise this requirement for areas with significant galloping history.
Damper Requirements | Intial unloaded tension 35% Final unloaded tension 25% | <18% RBS (No dampers required) 18%-20% RBS (Dampers required)
Spacers | Not Specified | 18" spacing - NO preformed wire spacers allowed
Approved conductor sizes for NEW construction | Not Specified | Match approved conductor sizes and bundle configuration with local utility company
Approved static and OPGW wires sizes for NEW construction | Not Specified | Match approved conductor sizes with the TO
Ratings of conductors | Not Specified | PJM TSDS Bare Overhead Transmission Conductor Ratings, November 2000
Conductor Operation Temperature and Conductor Sag | Not Specified
Min Conductor Operating Temp for Sagging and Clearance Purposes | Not Specified | ACAR - 100ᴼC ACSR, ACSS - 125ᴼC
Maximum Operating Temperature | Not Specified | ACAR - 140ᴼC ACSR, ACSS - 180ᴼC
Right-Of-Way width (Target values) | Not Specified | 150 Ft - 1 & 2 CKT
Max. Number of circuits per structure | Not Specified | 2 unless specifically approved by TO
Min. design ground clearance at Max. sag | NESC Rule 232 | NESC minimum requirements PLUS an additional 3 feet
Conductor to structure steel clearance (min.) | NESC Rule 235 | 69 in all anticipated conductor positions from an every day condition to a displaced conductor due to 9 psf wind or ice loading, based on 2.4 per unit switching surge values
Wire-to-wire clearances | NESC Rule 233 | Min. NESC Rule 233 and 235. trans wire calculated at max operating temp or heavy ice, whichever great sag and non-transmission wire at 0ᴼF
Clearances between transmission conductors | NESC Rule 233 | Larger of either 2.5 per unit switching surge or clearances based on NESC
Conductor Tension Limits
NESC 250B | 60% | Not Specified
NESC 250C | 80% | Not Specified
NESC 250D | 80% | Not Specified
Heavy Ice |  | Not Specified
No Wind, No Ice, 60ᴼF, Initial | 35% | Not Specified
No Wind, No Ice, 60ᴼF, Final | 25% | 18-20%
Insulation Requirements
Leakage Distance | Not Specified | 167 in
60 Hz Wet | Not Specified | 490 kV
Switching Surge | Not Specified | 2.5 per unit
Critical Impulse Flashover | Not Specified | 1105 kV
Maximum Structure Ground Resistance | Not Specified | 25 ohms. Individual tower ground measurements will be allowed to exceed if the avg value for the 5 adjacent structures along line is less than the 15 ohms
Step & Touch Potential Issues | Not Specified | Provide a structure grounding system that meets the step and touch requirements of the TO
Minimum Number of Static Wires Required | Not Specified | Minimum of 1 per circuit
Maximum Shielding Angle | Not Specified | 25ᴼ
EMF Limits | Not Specified | As Required by TO and State Regulatory Agencies EPRI ENVIRO or equiv software
Radio Interference at edge of right-of-way | Not Specified | Not specified
Audible Noise | Not Specified | Per applicable state laws for noise at edge of right-of-way Using wet conductor design condition
Voltage gradient | Not Specified | Not specified
Inductive interference | Not Specified | Not specified
Line transpositions | Not Specified | Not specified
STRUCTURAL
S1. Steel Structure Design Loading Conditions
a. NESC Heavy Loading District
Wind Pressure on wires (psf) | 4 | 4
Wind Pressure on structure (psf) | 4 | 4
Radial Ice (inches) | 0.5 | 0.5
Temperature (deg F) | 0 | 0
Load Constant (lbs) | 0.3 | 0.3
Load Factors | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65 | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65
b. NESC 250C Extreme Wind
Wind Pressure on wires (psf) | NESC 250C Wind Map | 25
Wind Pressure on structure (psf) | NESC 250C Wind Map | 31.25
Radial Ice (inches) | N/A | 0
Temperature (deg F) | 60 | 60
Load Constant (lbs) | N/A | N/A
Load Factors | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00 | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
c. NESC 250D Concurrent Wind & Ice
Wind Pressure (psf) | NESC 250D Wind and Ice Map | Not specified
Wind Pressure on structure (psf) | NESC 250D Wind and Ice Map | Not specified
Radial Ice (inches) | NESC 250D Wind and Ice Map | Not specified
Temperature (deg F) | NESC Table 250 | Not specified
Load Constant (lbs) | N/A | Not specified
Load Factors | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00 | Not specified
d. Heavy Ice
Wind Pressure (psf) | N/A | 0
Wind Pressure on structure (psf) | N/A | 0
Radial Ice (inches) | N/A | 1.5
Temperature (deg F) | N/A | 32
Load Constant (lbs) | N/A | N/A
Load Factors | Wind: N/A Vertical: N/A Tension: N/A | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
e. Longitudinal for Suspension
d.1. One broken conductor or static wire
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.10 Transverse: 1.10 Vertical: 1.10 Tension: 1.10
d.2. Differential ice loading
Wind Pressure (psf) | Not Specified | 0
Wind Pressure on structure (psf) | Not Specified | 0
Radial Ice (inches) | Not Specified | 1.0" one side/0" other side
Temperature (deg F) | Not Specified | 32
Load Constant (lbs) |  | N/A
Load Factors | Not Specified | Wind: 1.10 Wind on structure: 1.10 Vertical: 1.10 Tension: 1.10
d.3. Bound stringing block
Wind Pressure (psf) | Not Specified | 2
Wind Pressure on structure (psf) | Not Specified | 4
Radial Ice (inches) | Not Specified | 0
Temperature (deg F) | Not Specified | 30
Load Constant (lbs) | Not Specified | N/A
Load Factors | Not Specified | Wind: 2.0 Transverse: 2.0 Vertical: 2.0 Tension: 2.0
f. Longitudinal for Strain
f.1. One broken conductor or static wire
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.10 Transverse: 1.10 Vertical: 1.10 Tension: 1.10
f.2. All conductors and static wires broken
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 1.00 Transverse: 1.00 Vertical: 1.00 Tension: 1.00
g. Longitudinal for Dead End
Wind Pressure (psf) | Not Specified | 4
Wind Pressure on structure (psf) | Not Specified | 10
Radial Ice (inches) | Not Specified | 0.5
Temperature (deg F) | Not Specified | 0
Load Constant (lbs) | Not Specified | 0.3
Load Factors | Not Specified | Wind: 2.50 Transverse: 2.50 Vertical: 1.5 Tension: 1.65
h. Longitudinal for Line Termination | Not Specified | Same as Intact Conditions
CIVIL/FOUNDATIONS
Flood Plain | Not Specified | Meet applicable local, State and Federal Regulations
A. Drilled Pier (Caisson)
Design | Not Specified | Not specified
Foundation Diameter | Not Specified | Not specified
Foundation Reveal | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | 1.25 times the design factored load reactions for overturning moment and uplift foundations and 1.10 times the design factored loads for the compression foundations
Performance Criteria | Not Specified | Not specified
Concrete | Not Specified | Not specified
B. Directly Embedded Structure
Design | Not Specified | Not specified
Excavation Diameter | Not Specified | Not specified
Epoxy Coating | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | Not Specified
Performance Criteria | Not Specified | Not specified
Backfill | Not Specified | Not specified
B. Pile Foundation
Design | Not Specified | Not specified
Foundation Strength/Loading | Not Specified | Not Specified
Pile Performance Criteria | Not Specified | Not Specified
Concrete | Not Specified | Not Specified
C. Specialty Foundation
Design | Not Specified | Not Specified