## Setup
Enter Stakeholder Group Name in cell A2:
DER Subcommittee
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Public Distribution Microgrid

## 1. Interest Identification
DER Subcommittee
Public Distribution Microgrid
Interest Identification
Instructions: List interests of all parties on this page.
1 | Ensure PJM market rules recognize the unique configuration of front of meter generation that is able to island in the form of a microgrid.
2 | Ensure the distribution owner is aware of all aspects of the microgrid, including relaying configuration, modes of generation, islanding process
3 | Comparable treatment of wholesale resources (market power)
4 | Fully accounted for in resource adequacy
5 | Able to provide all wholesale services
6 | Methods can be adapted or leveraged for future use
7 | Flexible rules that allow for all existing and potential future ownership / operational structures of microgrids, including third party ownership and operation
8
9
10
11
12
13
14
15
16
17
18
19
20

## 2. Options Matrix- Design Comp.
DER Subcommittee
Public Distribution Microgrid
OPTIONS MATRIX
| Updated: May 18, 2020 |  | Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E
* | Implementation
1 | Definitions
1a | Microgrid |  |  | A Microgrid is a defined set of generation and load that can operate both while connected to and while islanded (i.e., isolated) from the broader grid. A microgrid must include load, one or more generators, one or more switches for isolating and connected to the broader grid, and a microgrid controller. A microgrid could include public utility distribution facilities. | Microgrid shall mean a defined set of generation and load that can operate both while connected to and while islanded (i.e., isolated) from the broader grid. A microgrid must include load, one or more generators, one or more switches for isolating and connected to the broader grid, and a microgrid controller. A microgrid could include public utility facilities.
1b | Public Distribution Microgrid |  | N/A | "A collection of generators and other resources, at least one of which is a PJM wholesale generator or energy storage resource, electric distribution company (EDC) grid facilities, and end use loads that can operate both grid-connected and islanded from the grid. It does not include any PJM-operated transmission facilities." In general, what differentiates a “Public Distribution Microgrid” from other microgrids is that it uses the EDC-owned facilities to island load and generation, rather than exclusively customer-owned facilities. | A Public Distribution Microgrid is a Microgrid that includes a PJM Generation Capacity Resource or Energy Resource that is capable of generating both while connected to and while islanded from the broader grid, and which also includes dual use utility distribution facilities. A Public Distribution Microgrid may not include any NERC Bulk Electric System components nor any Transmission System components that are controlled or operated by PJM. | "A collection of generators and other resources, at least one of which is a PJM wholesale generator or PJM wholesale energy storage resource, electric distribution company (EDC) grid facilities, and end use loads that can operate both grid-connected and islanded from the grid. It does not include any PJM-operated transmission facilities." When connected, a "Public Distribution Microgrid" is a PJM resource, when islanded a "Public Distribution Microgrid" is not a PJM resource. | Public Distribution Microgrid shall mean a Microgrid that includes a PJM Generation Capacity Resource or Energy Resource that is capable of generating both while connected to and while islanded from the broader grid, and which also includes dual use utility distribution facilities. A Public Distribution Microgrid may not include any NERC Bulk Electric System components nor any Transmission Facilities.
1c | Public Distribution Microgrid Operator |  | N/A | The entity who controls switch gear, relays, microgrid controller and other equipment required to island generation and load on the distribution system. | A Public Distribution Microgrid Operator is the Electric Distributor whose distribution facilities form part of the Public Distribution Microgrid. | A Public Distribution Microgrid Operator is an Electric Distributor that controls a Public Distribution Microgrid, or is a Member that has been designated to control a Public Distribution Microgrid on an Electric Distributor’s behalf. Control of a Public Distribution Microgrid means control of switch gear, relays, microgrid controller and other equipment required to island generation and load in a Public Distribution Microgrid. | Public Distribution Microgrid Operator shall mean an Electric Distributor that controls a Public Distribution Microgrid, or a Member that has been designated to control a Public Distribution Microgrid on an Electric Distributor’s behalf. Control of a Public Distribution Microgrid means control of switch gear, relays, microgrid controller and other equipment required to island generation and load in a Public Distribution Microgrid.
1d | Public Distribution Microgrid Generator |  | N/A | Public Distribution Microgrid Generator is a PJM wholesale generator that also has the ability to directly serve load as part of a Public Distribution Microgrid when islanded. | A Public Distribution Microgrid Generator is any share of a generator in the Public Distribution Microgrid that is a Generation Capacity Resource or Energy Resource and that is capable of generating both while connected to and while islanded from the broader grid. This term includes Energy Storage Resources. | Public Distribution Microgrid Generation is a PJM wholesale generator or PJM wholesale energy storage resource that also has the ability to directly serve load as part of a Public Distribution Microgrid when islanded. | Public Distribution Microgrid Generator is any share of a generator in a Public Distribution Microgrid that is a Generation Capacity Resource or Energy Resource and that is capable of generating both while connected to and while islanded from the broader grid. This term includes Energy Storage Resources.
2 | Energy Market Settlement
2a | Grid connected mode |  | Generation and Load settled at LMP through Power Meter and InSchedules, respectively. | Reduction in output due to islanding, or other reason to not meet energy schedule, subject to deviation charges.
2b | Settlements of islanded MWh supply and demand |  | EDC is responsible for quantifying PJM load in their zone, and for approving submissions of PJM quantities in their zone. | Public Distribution Microgrids settle islanded wholesale generation MWh output and LSE MWh load purchases through PJM markets, same as grid connected mode | Load and generation settled locally within the microgrid
3 | Microgrid LMP when islanded |  | Generation settled at associated pnode, Load settled at zonal average LMP | The normal process would apply if the microgrid only formed a portion of a PJM load node (which is likely) and if that PJM load node were still partly operating normally. In that case, it might look to PJM like the power withdrawal at that node is simply reduced by the amount of the islanded load, while the PJM generation at the applicable node is increased by the amount of the online microgrid generation, and all load could continue to be settled normally by the applicable LMP. | No longer wholesale power when islanded. Generation and load settled not settled PJM.
4 | Generation status when in island mode |  | N/A | Unit should self-schedule (Availability in Markets Gateway = Must Run) and be logged as "company non-dispatchable” so that SCED will not attempt to dispatch the unit when islanded | Unit is not available, on outage
5 | Ancillary Services eligibility when islanded |  | N/A | When in island mode, Microgrid Generation will be de-assigned from any existing Ancillary Services commitments and performance will be assessed as normal. | When in island mode, Microgrid Generation will be deassigned from any existing Ancillary Services commitments and face any penalties associated with deassignment | When in island mode, an operator of a Public Distribution Microgrid Generator shall de-assign it from any existing Ancillary Services commitments (performance will be assessed as normal), and shall ensure it is not assigned for ancillary services for future intervals unless it is certain it will not be islanded in those intervals.
6 | RPM Offer Requirement |  | Public Distribution Microgrid generator subject to offer requirement as described in OATT Attachment DD Section 6.6
7 | Performance Assessment Interval calculation for Generation Capacity Performance Resource when islanded |  |  | Any generation MWh output that is settled through the PJM energy market counts towards Capacity Performance obligation. The expected output during a PAI is what it would have been had the generator still been grid connected. | Whether or not the unit is settled through PJM energy market, it still has an obligation if it is a capacity resource | Unit is not available, generation MWh not counted towards Capacity Performance obligation
8 | Telemetry requirements |  | Existing requirements in M14D | In addition to existing telemetry requirements, a Public Distribution Microgrid Operator shall provide status of any switching and/or relay that indicates the status of the Public Distribution Microgrid (i.e.. Open, closed, island, etc.) | A Public Distribution Microgrid Generator shall meet existing telemetry requirements for all PJM generators. In addition, if it has real-time data on whether it is islanded or not, it shall provide that data to PJM. A Public Distribution Microgrid Operator shall provide to Public Distribution Generators the real-time status of any switching and/or relay that indicates the status of the Public Distribution Microgrid (i.e.. Open, closed, island, etc.).
9 | Special provisions for islanding |  | N/A | A Public Distribution Microgrid Operator shall not "Economically island." The only acceptable reasons for the Public Distribution Microgrid Operator to island include: 1. An emergency situation on the distribution and/or transmission system, or a situation impacting system restoration; 2. An emergency situation on the transmission system, as defined by PJM Emergency Procedures, in which load shedding action is directed by PJM 3. Emergency declaration by appropriate local, state, or federal authority 4. Testing 5. Distribution facility maintenance After islanded, a Public Distribution Microgrid Operator must reconnect the Public Distribution Microgrid as soon as reasonably possible. | A Public Distribution Microgrid Generator shall notify PJM of the start and end of an islanded condition as soon as practicable, based on if and when it is aware of it. This could include advance notification of planned or scheduled islanding, real time notification of actual islanding, and ex-post data on islanding. If possible, a Public Distribution Microgrid Operator should notify a Public Distribution Generator, the Interconnected Transmission Owner, and PJM of that start and end of an islanded condition as soon as practicable. | The Public Distribution Microgrid Generator operator shall notify PJM of the start and end of planned and actual islanded conditions as soon as practicable. To facilitate that notification, the Public Distribution Microgrid Operator shall provide all necessary information to the Public Distribution Microgrid Generator operator on an ongoing basis.
10 | Outage reporting in island mode |  | N/A | If a Public Distribution Microgrid Generator’s full ICAP MW is physically available and is only constrained because it is in island mode, no unplanned outage needs to be reported and the generator can be listed as fully available. If the Public Distribution Microgrid Generator is limited to less than its ICAP MW while serving load, an unplanned outage should be reported. | If the Public Distribution Microgrid Generator has a forced outage or de-rate and is therefore limited to less than its ICAP MW while serving load, an unplanned outage should be reported. | Generator has a forced outage when islanded | In eDART, the Public Distribution Microgrid Generator should report a full outage. In GADS, if a Public Distribution Microgrid Generator's full ICAP MW is physically available and is only constrained because it is in island mode, no unplanned outage needs to be reported and the microgrid generator can be listed as fully available. If the microgrid generator is limited to less than its ICAP MW while serving load, due to reasons other than being constrained by the total load in the island, an unplanned outage should be reported. Such units serve PJM load when islanded, and therefore there is no impact to EFORd due solely to islanding status. | In eDART, the Public Distribution Microgrid Generator should report a full outage. In GADS, if a Public Distribution Microgrid Generator's full ICAP MW is physically available and is only constrained because it is in island mode, no unplanned outage needs to be reported and the microgrid generator can be listed as fully available. If the microgrid generator is limited to less than its ICAP MW while serving load, due to reasons other than being constrained by the total load in the island, an unplanned outage should be reported in GADS. PJM will use reporting on islanding status to calculate an EFORd for Public Distribution Microgrid Generators consistent with such units being unavailable to serve PJM load when islanded.
11 | Interconnection agreement |  | WMPA (non-jurisdictional), or ISA (jurisdictional) | non-standard WMPA or ISA language
11a | Planning process |  | N/A | A Transmission Owner that is planning or has an affiliate that is planning a Public Distribution Microgrid with automatic separation shall should, if possible, provide PJM with the details of how the relay would automatically open the switch.
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attribute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
DER Subcommittee
Public Distribution Microgrid
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
DER Subcommittee
Public Distribution Microgrid
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
DER Subcommittee
Public Distribution Microgrid
PACKAGE/ PROPOSAL MATRIX
Formatted to print 1 pg wide x 2 pg long
| Updated: August 3, 2020 |  | Packages
# | Design Components | Priority | Status Quo | A (removed) | B (removed) | C (Package A revised) | D
1 | Definitions
1a | Microgrid |  | N/A | Option A: A Microgrid is a defined set of generation and load that can operate both while connected to and while islanded (i.e., isolated) from the broader grid. A microgrid must include load, one or more generators, one or more switches for isolating and connected to the broader grid, and a microgrid controller. A microgrid could include public utility distribution facilities. | Same as A | Option A: A Microgrid is a defined set of generation and load that can operate both while connected to and while islanded (i.e., isolated) from the broader grid. A microgrid must include load, one or more generators, one or more switches for isolating and connected to the broader grid, and a microgrid controller. A microgrid could include public utility distribution facilities.
1b | Public Distribution Microgrid |  | N/A | Option B: A Public Distribution Microgrid is a Microgrid that includes a PJM Generation Capacity Resource or Energy Resource that is capable of generating both while connected to and while islanded from the broader grid, and which also includes dual use utility distribution facilities. A Public Distribution Microgrid may not include any NERC Bulk Electric System components nor any Transmission System components that are controlled or operated by PJM. | When connected, a "Public Distribution Microgrid" is a PJM resource, when islanded a "Public Distribution Microgrid" is not a PJM resource. | Option D: Public Distribution Microgrid shall mean a Microgrid that includes a PJM Generation Capacity Resource or Energy Resource that is capable of generating both while connected to and while islanded from the broader grid, and which also includes dual use utility distribution facilities. A Public Distribution Microgrid may not include any NERC Bulk Electric System components nor any Transmission Facilities.
1c | Public Distribution Microgrid Operator |  | N/A | Option C: A Public Distribution Microgrid Operator is an Electric Distributor that controls a Public Distribution Microgrid, or is a Member that has been designated to control a Public Distribution Microgrid on an Electric Distributor’s behalf. Control of a Public Distribution Microgrid means control of switch gear, relays, microgrid controller and other equipment required to island generation and load in a Public Distribution Microgrid. | Same as A | Option D: Public Distribution Microgrid Operator shall mean an Electric Distributor that controls a Public Distribution Microgrid, or a Member that an Electric Distributor has been designated to control a Public Distribution Microgrid on an Electric Distributor’s behalf. Control of a Public Distribution Microgrid means control of switch gear, relays, microgrid controller and other equipment required to island generation and load in a Public Distribution Microgrid.
1d | Public Distribution Microgrid Generator |  | N/A | Option B: A Public Distribution Microgrid Generator is any share of a generator in the Public Distribution Microgrid that is a Generation Capacity Resource or Energy Resource and that is capable of generating both while connected to and while islanded from the broader grid. This term includes Energy Storage Resources. | Same as A | Option D: Public Distribution Microgrid Generator is any share of a generator in a Public Distribution Microgrid that is a Generation Capacity Resource or Energy Resource and that is capable of generating both while connected to and while islanded from the broader grid. This term includes Energy Storage Resources.
2 | Energy Market Settlement
2a | Grid connected mode |  | Generation and Load settled at LMP through Power Meter and InSchedules, respectively. | Status quo | Status Quo | Status Quo
2b | Settlements of islanded MWh supply and demand |  | EDC is responsible for quantifying PJM load in their zone, and for approving submissions of PJM quantities in their zone. | Option A: Public Distribution Microgrids settle islanded wholesale generation MWh output and LSE MWh load purchases through PJM markets, same as grid connected mode | Load and generation settled locally within the microgrid | Status Quo (EDC determines if PDM is wholesale or retail when islanded)
3 | Microgrid LMP when islanded |  | Generation settled at associated pnode, Load settled at zonal average LMP | Option A: The normal process would apply if the microgrid only formed a portion of a PJM load node (which is likely) and if that PJM load node were still partly operating normally. In that case, it might look to PJM like the power withdrawal at that node is simply reduced by the amount of the islanded load, while the PJM generation at the applicable node is increased by the amount of the online microgrid generation, and all load could continue to be settled normally by the applicable LMP. | No longer wholesale power when islanded. | If EDC determines PDM is wholesale when islanded: Status Quo If EDC determines PDM is retail when islanded: Option B, Generation and load settled not settled by PJM.
4 | Generation status when in island mode |  | N/A | Option A: Unit should self-schedule (availability in Markets Gateway = Must Run) and be logged as “company non-dispatchable” so that SCED will not attempt to dispatch the unit when islanded. | Unit is not available, on outage | If EDC determines PDM is wholesale when islanded: Option A, Unit should self-schedule (availability in Markets Gateway = Must Run) and be logged as “company non-dispatchable” so that SCED will not attempt to dispatch the unit when islanded. If EDC determines PDM is retail when islanded: Option B, unit is not available
5 | Ancillary Services eligibility when islanded |  | N/A | Solution A: When in island mode, Microgrid Generation will be de-assigned from any existing Ancillary Services commitments and performance will be assessed as normal. | Same as A | Whether wholesale or retail when islanded: Option C, When in island mode, an operator of a Public Distribution Microgrid Generator shall de-assign it from any existing Ancillary Services commitments (performance will be assessed as normal), and shall ensure it is not assigned for ancillary services for future intervals unless it is certain it will not be islanded in those intervals.
6 | RPM Offer Requirement |  | Public Distribution Microgrid generator subject to offer requirement as described in OATT Attachment DD Section 6.6 | Status quo | Status Quo | Status Quo
7 | Performance Assessment Interval calculation for Generation Capacity Performance Resource when islanded |  |  | Option A: Any generation MWh output that is settled through the PJM energy market counts towards Capacity Performance obligation. The expected output during a PAI is what it would have been had the generator still been grid connected. | Option C: Unit is not available, generation MWh not counted towards Wholesale Capacity Requirement | If EDC determines PDM is wholesale when islanded: Option A, Any generation MWh output that is settled through the PJM energy market counts towards Capacity Performance obligation. The expected output during a PAI is what it would have been had the generator still been grid connected. If EDC determines PDM is retail when islanded: Option C. Unit is not available, generation MWh not counted towards Capacity Performance obligation
8 | Telemetry requirements |  | Existing requirements in M14D | Option A: In addition to existing telemetry requirements, a Public Distribution Microgrid Operator shall provide status of any switching and/or relay that indicates the status of the Public Distribution Microgrid (i.e.. Open, closed, island, etc.) | Same as A Option B: A Public Distribution Microgrid Generator shall meet existing telemetry requirements for all PJM generators. In addition, if it has real-time data on whether it is islanded or not, it shall provide that data to PJM. A Public Distribution Microgrid Operator shall provide to Public Distribution Generators the real-time status of any switching and/or relay that indicates the status of the Public Distribution Microgrid (i.e.. Open, closed, island, etc.). | Option B: A Public Distribution Microgrid Generator shall meet existing telemetry requirements for all PJM generators. In addition, if it has real-time data on whether it is islanded or not, it shall provide that data to PJM. A Public Distribution Microgrid Operator shall provide to Public Distribution Generators the real-time status of any switching and/or relay that indicates the status of the Public Distribution Microgrid (i.e.. Open, closed, island, etc.).
9 | Special provisions for islanding |  | N/A | Option A: A Public Distribution Microgrid Operator shall not "economically island”. The only acceptable reasons for the Public Distribution Microgrid Operator to island include: 1. An emergency situation on the distribution and/or transmission system, or a situation impacting system restoration; 2. An emergency situation on the transmission system, as defined by PJM Emergency Procedures, in which load shedding action is directed by PJM 3. Emergency declaration by appropriate local, state, or federal authority 4. Testing 5. Distribution facility maintenance After islanded, a Public Distribution Microgrid Operator must reconnect the Public Distribution Microgrid as soon as reasonably possible. | Option A: A Public Distribution Microgrid Operator shall not "economically island”. The only acceptable reasons for the Public Distribution Microgrid Operator to island include: 1. An emergency situation on the distribution and/or transmission system, or a situation impacting system restoration; 2. An emergency situation on the transmission system, as defined by PJM Emergency Procedures, in which load shedding action is directed by PJM 3. Emergency declaration by appropriate local, state, or federal authority 4. Testing 5. Distribution facility maintenance After islanded, a Public Distribution Microgrid Operator must reconnect the Public Distribution Microgrid as soon as reasonably possible. | Option C: The Public Distribution Microgrid Generator operator shall notify PJM of the start and end of planned and actual islanded conditions as soon as practicable. To facilitate that notification, the Public Distribution Microgrid Operator shall provide all necessary information to the Public Distribution Microgrid Generator operator on an ongoing basis. Option A added as a voluntary guideline to PJM business manual. A Public Distribution Microgrid Operator shall not "economically island”. The only acceptable reasons for the Public Distribution Microgrid Operator to island include: 1. An emergency situation on the distribution and/or transmission system, or a situation impacting system restoration; 2. An emergency situation on the transmission system, as defined by PJM Emergency Procedures, in which load shedding action is directed by PJM 3. Emergency declaration by appropriate local, state, or federal authority 4. Testing 5. Distribution facility maintenance After islanded, a Public Distribution Microgrid Operator must reconnect the Public Distribution Microgrid as soon as reasonably possible.
10 | Outage reporting in island mode |  | N/A | Option A: If a Public Distribution Microgrid Generator's full ICAP MW is physically available and is only constrained because it is in island mode, no unplanned outage needs to be reported and the microgrid generator can be listed as fully available. If the microgrid generator is limited to less than its ICAP MW while serving load, an unplanned outage should be reported. | Option B: Generator has a forced outage when islanded. Generator operator coordinates with switch operator during islanding test and submits an eDART ticket. Limit the number of scheduled tests. | If EDC determines PDM is wholesale when islanded: Option D. In eDART, the Public Distribution Microgrid Generator should report a full outage. In GADS, if a Public Distribution Microgrid Generator's full ICAP MW is physically available and is only constrained because it is in island mode, no unplanned outage needs to be reported and the microgrid generator can be listed as fully available. If the microgrid generator is limited to less than its ICAP MW while serving load, due to reasons other than being constrained by the total load in the island, an unplanned outage should be reported. Such units serve PJM load when islanded, and therefore there is no impact to EFORd due solely to islanding status. If EDC determines PDM is retail when islanded: Option E. In eDART, the Public Distribution Microgrid Generator should report a full outage. In GADS, if a Public Distribution Microgrid Generator's full ICAP MW is physically available and is only constrained because it is in island mode, no unplanned outage needs to be reported and the microgrid generator can be listed as fully available. If the microgrid generator is limited to less than its ICAP MW while serving load, due to reasons other than being constrained by the total load in the island, an unplanned outage should be reported in GADS. PJM will use reporting on islanding status to calculate an EFORd for Public Distribution Microgrid Generators consistent with such units being unavailable to serve PJM load when islanded.
11 | Interconnection agreement |  | WMPA (non-jurisdictional), or ISA (jurisdictional) | Status quo | Status Quo | Status Quo
12 | Planning process |  | N/A | A Transmission Owner that is planning or has an affiliate that is planning a Public Distribution Microgrid with automatic separation shall provide PJM with the details of how the relay would automatically open the switch. | A Transmission Owner that is planning or has a distribution affiliate that is planning a Public Distribution Microgrid with automatic separation shall provide PJM with the details of how the relay would automatically open the switch. | A Transmission Owner that is planning or has a distribution affiliate that is planning a Public Distribution Microgrid with automatic separation shall should, if possible, provide PJM with the details of how the relay would automatically open the switch.
Low - High
Medium
Instructions: | [7 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [7 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
DER Subcommittee
Public Distribution Microgrid
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
DER Subcommittee
Public Distribution Microgrid
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
DER Subcommittee
Public Distribution Microgrid
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3