## DLRTF Education Tracker
# | Education Request | Date Contributed | Category | Responses (with links tor previous Education, PJM Manuals, and FERC Materials where applicable) | Response Updated
1 | What is the status of an order from FERC related to DLRs? | Education Survey, closed 10/12/2022 | DLR Implementation | FERC Notice of Inquiry [NOI] remains open since February 17, 2022 (Item No. E-1, Docket AD22-5-000) on the Implementation of Dynamic Line Ratings. PJM response to the NOI can be found here. https://www.pjm.com/-/media/documents/ferc/filings/2022/20220509-ad22-5-000.ashx | 2022-11-09
2 | Does PJM require DLRs to be installed on any or all lines, or will Transmission Owners decide? | Education Survey, closed 10/12/2022 | DLR Implementation | There is no FERC or PJM requirement to install DLR on any facility. Transmission Owners decide where DLR technology will be deployed. PJM maintains systems and procedures to allow TOs to implement DLR if a TO chooses to do so. As of October 2022, FERC has noted that DLR is an option for a Transmission Owner, and that RTO/ISO must establish and maintain systems and procedures necessary to allow TOs to update ratings at minimum hourly. Once ruled upon, the 2/17/2022 inquiry around DLR implementation may give further insight here as to projected DLR penetration. PJM response to the NOI can be found here: https://www.pjm.com/-/media/documents/ferc/filings/2022/20220509-ad22-5-000.ashx See education from 9/30/2022 DLRTF: https://www.pjm.com/-/media/committees-groups/task-forces/dlrtf/2022/20220930/item-04---dlr-in-pjm-to-date.ashx | 2022-11-09
3 | What are the notfication timelines and steps for DLR implementation in PJM? | Education Survey, closed 10/12/2022 | DLR Implementation | DLR implementation notification requirements, including the initiating step of PJM member awareness via the PJM Operating Committee, are captured in M-03, Section 2.1.1.2. Additional steps would include eDART DLR facility identification, and addtional coordination between PJM and to the DLR prospective-owner. For a full list of manual requirement changes related to DLR, please see https://www.pjm.com/-/media/committees-groups/committees/oc/2022/20220310/20220310-item-06a-manual-01-manual-03-and-manual-03a-updates-executive-summary.ashx. | 2022-11-09
4 | What are the data and communication requirements between DLR field devices, TO Systems and PJM systems? | Education Survey, closed 10/12/2022 | DLR Implementation | The inputs and measurements needed when calculating DLRs are not mandated by PJM. The TO makes these decisions with the DLR vendor of their choice, based on their Rating Methodology and the vendor's product capabilities. The communication between the field devices and TO's EMS, and other technical requirements related to that are dependent upon on the vendor's product and the individual TO systems/methodology. PJM requires real-time dynamic line ratings to be received via EMS Datalinks (i.e. ICCP) and forecasted hourly dynamic line ratings via eDART TERM (see Manual 03, Section 2.1.1.2). DLR does not change the need to communicate and coordinate ratings. For a full list of PJM communication requirements related to DLRs, please see https://www.pjm.com/-/media/committees-groups/committees/oc/2022/20220310/20220310-item-06a-manual-01-manual-03-and-manual-03a-updates-executive-summary.ashx and related manuals. | 2022-11-09
5 | Does PJM have any limitations when it comes to DLR implementation on TO facilities? | Education Survey, closed 10/12/2022 | DLR Implementation | The confines of PJM's present abilities to incorporate DLR are as follows: PJM's projected 2023+ EMS systems are restricted to a hard limit of 200 DLR facilities, absent SCADA-functional enhancement; true DLR-technology is restricted to that of "lines" as it is conductor-based, however no PJM-systematic restrictions inhibit DLR from being applied against any thermally rated facility (lines, transformers, series devices, phase angle regulators & flow devices). An additional limitation at the moment is the incorporation of DLR into reliability studies is at present a manual data entry approach, which is alleviated by situational awareness tools and the limited implementation to 3 facilities. Automation will be incorporated due to FERC Order 881 driven changes and/or additional DLR implementation notices, whichever comes first. | 2022-11-09
6 | Can the TOs share their DLR implementation experiences, challenges, benefits, outcomes? Vendors and technologies used? Implementation costs and timeframes? Any operational, IT, data communication challenges? | Education Survey, closed 10/12/2022 | DLR Implementation | PJM encourages DLR owners & DLR pilot-users to share their experiences with PJM members as they see fit while respecting their vendor agreements. This is a topic for future education. | 2022-11-09
7 | Can PJM share their DLR implementation experiences, challenges, benefits, outcomes, etc.? Any operational, IT, data communication challenges? | Education Survey, closed 10/12/2022 | DLR Implementation | The initial DLR implementation created educational challenges, in addition to requiring retooling around past DLR-functional enhancements to account for the throughput of modern DLR versus that of past dynamic ratings experiences with facilities like Waldwick. Additional experience related to PPL's DLR implementation on October 6, 2022 is a topic for future eduction. | 2022-11-09
8 | Is sample data available for a DLR implementation and impacts on ratings? | Education Survey, closed 10/12/2022 | DLR Implementation | DLR are not always higher and are sometimes lower than traditional rating methods. One substantive factor that can drive significant increases in ratings for a DLR facility that is primarily conductor-limited would be wind-direction & speed, which for traditional methods must be given conservative assumptions which may not match near-term forecasted and actual weather conditions. PPL's DLR implementation occured on October 6, 2022, initiating substantive real world experience in PJM. PJM encourages DLR owners & DLR pilot-users to share their experiences with PJM members. This is a topic for future education. Data from a PJM pilot projects with AEP and LineVision are available here: https://www.pjm.com/-/media/committees-groups/forums/emerging-tech/2020/20200827/20200827-item-05-dynamic-line-ratings.ashx | 2022-11-09
9 | Is there/should there be activity in Transmission & Substation Subcommittee (TSS) to develop PJM guidance/requirements for implementation of DLR in PJM? Is there a need to develop some consistency of implementation? | Education Survey, closed 10/12/2022 | DLR Implementation | While there are currently no plans for TSS to develop guidance/requirements for implementation of DLR in PJM, TSS has been tracking DLR technology with a focus on equipment installation, O&M and potential guideline updates. Impacts DLR implementation are within the scope of DLRTF, but DLR equipment installation and O&M could be within the scope of TSS. | 2022-11-09
10 | Will PJM update the PJM guideline on the Bare Conducting Rating Manual for DLR implementation and rating determination requirements? When? | Education Survey, closed 10/12/2022 | DLR Implementation | No, the mentioned guide is not related to DLR implementation. PJM Transmission & Substation Subcommittee (TSS) has a Special Session on OHL Rating Guide review this year. | 2022-11-09
11 | For members with facilities in different incumbent member areas, do the facilities need to match the assumptions of the incumbent TO? | Education Survey, closed 10/12/2022 | DLR Implementation | No. Agreements, assumptions & requirements between neighboring TO facilities with regard to Facility Ratings are unchanged by DLR. | 2022-11-09
12 | What are the real-time impacts of DLR? | Education Survey, closed 10/12/2022 | Impacts to System Operations | Within Day Ahead & Real-time, TO-provided DLR will adjust ratings at minimum hourly. As ratings will be derived closer to their use, they will encompass more accurate projections/actuals rather than an assumed weather condition that goes into traditional ratings. If the conductor is the restriction, the thermal Facility ratings associated with a DLR Facility would then be expected to increase on average. For a full list of manual requirement changes related to DLR, please see https://www.pjm.com/-/media/committees-groups/committees/oc/2022/20220310/20220310-item-06a-manual-01-manual-03-and-manual-03a-updates-executive-summary.ashx. | 2022-11-09
13 | Updates to eDart to accommodate DLR updates? | Education Survey, closed 10/12/2022 | Impacts to System Operations | eDART's TERM application DLR functional enhancements were required ahead of PPL's DLR Go-Live on 10/6/2022. For a non-DLR owner, eDART communicates DLR changes via PJM OASIS updates posted along with other thermal ratings information. (See https://www.pjm.com/markets-and-operations/etools/oasis/system-information/ratings-information) Future changes, if needed, will be communicated via eDART & PJM Tech Change forums. For a full list of manual requirement changes related to DLR, please see https://www.pjm.com/-/media/committees-groups/committees/oc/2022/20220310/20220310-item-06a-manual-01-manual-03-and-manual-03a-updates-executive-summary.ashx. | 2022-11-09
14 | How is PJM’s EMS going to be updated to account for multiple temperature sets? | Education Survey, closed 10/12/2022 | Impacts to System Operations | DLR itself does not drive any temperature set changes. This question appears to allude to FERC Order 881 around Ambient Adjusted Ratings. Changes such as this will be communicated via PJM stakeholder channels including the OC, eDART & Tech Change Forums. See the October 2022 OC for a recent update example in this space, particularly Slide 7: https://www.pjm.com/-/media/committees-groups/committees/oc/2022/20221007/item-13---ferc-order-881-update.ashx | 2022-11-09
15 | NERC standards require operating to the most conservative limit when discrepancies exist. - Have these protocols been considered going forward as limits could be more limiting based on data quality or regional component limitations (PJM and TO)? - How will conductor and non-conductor ratings be checked so that non-conductor-limited lines are not affected and the most limiting device is calculated? | Education Survey, closed 10/12/2022 | Impacts to System Operations | The most conservative limit is still embedded within NERC ratings & operating standards. A Transmission Owner's Ratings Methodology must incorporate all elements within the determination of the most limiting element that drives a given composite facility rating. This applies to DLR as well as all rating methodologies and transmission operating requirements. Additional information is captured in PJM's Transmissison Operating Procedures manual, M-03B. Additional topics in this space may be impacted by FERC Order 881. | 2022-11-09
16 | What is PJM’s process for planned switching between DLR and AAR for a single Facility or multiple Facilities? What notice will PJM require from a TO before switching between DLR and AAR? If an affected Facility is a lie-tine between TOs, how will this switching be coordinated between the TOs and PJM? | Education Survey, closed 10/12/2022 | Impacts to System Operations | For planned outages, awareness should be provided similar to other telecommunications maintenance. More details can be found in M01 (Control Center and Data Exchange Requirements), Section 3.8.1. For an individual DLR facility outage, the DLR outage notice can be further communicated within the eDART Description of Work field related to the given transmission ticket. If no such ticket exists otherwise, an informational ticket can be created to address the communication/coordination requirements on tie-lines. In addition to other known facilities with impact to a neighboring TO, tie line work must be coordinated with the neighbor. Per PJM's Transmission Operations manual, M-03, Section 1.5.4, tie lines are identified as Reportable and require coordination of switching and system security (which includes ratings.) In cases of unplanned outages to DLR systems, TO operator shall notify PJM dispatch of the outage, and discuss temporary solutions. Please M03 Section 2.1.1.2 for more details. | 2022-11-09
17 | How is DLR data validated? What happens should communications fail between the DLR equipment and PJM? Does PJM fall back to the AAR tables already being provided? | Education Survey, closed 10/12/2022 | Impacts to System Operations | Responses for the DLR facility owner and PJM can include monitoring for momentary service interruptions, coordination on use of last good value or forecated ratings, or fall back to traditional methods such as Lookup Tables (permanent TERM Tickets). For a full list of manual requirement changes related to DLR, please see https://www.pjm.com/-/media/committees-groups/committees/oc/2022/20220310/20220310-item-06a-manual-01-manual-03-and-manual-03a-updates-executive-summary.ashx. | 2022-11-09
18 | How are discrepancies addressed between control areas (outside PJM) and internal TOs? | Education Survey, closed 10/12/2022 | Impacts to System Operations | Processes for handling rating discrepancies between PJM, its members, and areas outside of PJM will not change as a result of DLR implemenation. | 2022-11-09
19 | How PJM address any potential overload issues / risks due to system malfunction and pre-existing line conditions? | Education Survey, closed 10/12/2022 | Impacts to System Operations | PJM approach to thermal "overloads" (i.e., exceedences and violations) are captured within the PJM Transmission Operations manual, M-03, Section 2. The approach remains true regardless of TO Ratings Methodology. Fallback approaches due to system failure for DLR are captured within Section 2.1.1.2. | 2022-11-09
20 | How will PCLLRW protocols change as a result of DLR implementation? | Education Survey, closed 10/12/2022 | Impacts to System Operations | DLR ratings are incorporated into the PCLLRW functionality. DLR facilities will be handled the same as all other PCLLRW facilities. | 2022-11-09
21 | Prior to discussing the DLR implementation in ARR/FTR markets, PJM should provide a detailed review of their current methodology for calculating effective facility ratings in ARR/FTR model. In particular, it would be good to gain clarity on: (a) Under what circumstances PJM does NOT use 95 degree facility ratings in their ARR/FTR model? (b) How does PJM derive the effective ratings in these circumstances? (c) Does PJM adjust ratings over the course of the planning period following ARR allocation? How/under what circumstances they are being adjusted? | Education Survey, closed 10/12/2022 | Impact to ARR/FTR Markets | Section 7.5(b) of Attachment K – Appendix of the OATT offers language in regards to ratings and why market limits can differ from operational limits as well as the factors causing adjustments. a. During the annual process, FTR/ARR operators will check historical congestion and reduce selected high congestion facilities’ ratings, called “uncompensated parallel flow” and published them under the FTR/ARR landing page on pjm.com. b. Normal rating change will come through the EMS model updates. Other rating updates can be adjusted by FTR/ARR opertors based on historical profile and other modeling inputs such as outages etc... c. During the auction setup, the recent DA case’s rating is an input to the model and it may and can change model ratings in accordance to the DA case | 2022-11-09
22 | What are the impact of DLR on FTR market auctions? | Education Survey, closed 10/12/2022 | Impact to ARR/FTR Markets | FTR/ARR Market is proceeding with status quo until a reasonable history of DLR performance is established. So today, the implementation of DLRs will have no impact on FTR markets. PJM will notify stakeholders if a DLR facility rating will change from the modeled rating in the Annual or the previous Monthly auction. A new posting for DLR facility rating update will be made available under the FTR landing page on PJM.com. See education from 9/30/2022 DLRTF: https://www.pjm.com/-/media/committees-groups/task-forces/dlrtf/2022/20220930/item-05---dlr-implementation-impact-to-arr-ftr-markets.ashx | 2022-11-11
23 | Does PJM have a comparison between the forecasted DLR for ARR/FTR markets and the real time DLR for a same period? How will DLRs be used beyond the operational horizon and into the Planning horizon for ARR/FTR markets? | Education Survey, closed 10/12/2022 | Impact to ARR/FTR Markets | No. Once a DLR historical profile is established, the FTR/ARR team will perform an analysis to determine if existing ratings will need to be adjusted in future FTR/ARR markets. PJM will notify stakeholders if a DLR facility rating will change from the modeled rating in the Annual or the previous Monthly auction. A new posting for DLR facility rating update will be made available under the FTR landing page on PJM.com. | 2022-11-11
24 | How will DLR impact seasonal ratings utilized in PJM planning studies? - Is PJM planning to modify the cases to now consider different temperature sets occurring at the same time? - Does PJM plan for the TOs to submit all 16 temperature dependent ratings now in PSS/E for line ratings? - How do we update PSS/E – RTEP and MMWG models to account for DLR? | Education Survey, closed 10/12/2022 | Impact to Seasonal Ratings utilized in PJM planning processes | In response to comment on Docket RM20–16–001, FERC clarified that, “None of the requirements in Order No. 881 require revisions to the assumptions used in the transmission planning and development contexts.” PJM plans to continue to leverage Summer/Winter Seasonal Ratings. These ratings will be pulled from the set of ratings submitted via PJM Operations practices through tools like PJM’s eDART: TERM functionality. While the available rating sets will expand, PJM Planning will continue to utilize Summer/Winter Seasonal Ratings for its analysis. Based on this clarification, along with existing procedures documented in M14B, PJM will continue to use the existing process for the determination of facility ratings. PJM Planning analysis defines ratings based on season. Summer and Winter: Ratings defined by temperature set data. - PJM Manual 14B Attachment B.3: “The published line and transformer daytime thermal ratings at ambient temperatures of 50F (10C) winter and 95F (35C) summer will be used as the default rating sets for all facilities.” Light Load: Ratings calculated based on Summer ratings - PJM Manual 14B 2.3.11: “The 50% of 50/50 summer peak demand level was chosen as being representative of an average light load condition.” See PJM Manual 14B Attachment B.3 and Section 2.3.11; and 9/30/2022 DLRTF Education: https://www.pjm.com/-/media/committees-groups/task-forces/dlrtf/2022/20220930/item-06---dlr-planning-impacts.ashx | 2022-11-09