## Current Mechanisms
Mechanism | Description | Objective | Time Period | Requirements | How is the Requirement Calculated? | Uncertainties Addressed | Resource / Fuel Eligibility | Compensation | Potential Fuel Security Gap (tbd)
Capacity Performance (CP) | Capacity construct that incentivizes performance and sets an obligation to perform for committed Capacity Resources during Emergency Actions throughout the Delivery Year. | Meet PJM's resource adequacy goals with resources capable of performing when needed during Emergency Actions. | Capacity commitments made up to 3 years in advance of the Delivery Year through the BRA. Performance measured in RT during PJM Emergency Actions at any time of the year. | Set by the VRR curve, which is anchored around the RTO or LDA Reliability Requirement. Committed resources are obligated to perform during Emergency Actions and required to offer in the Energy Market, subject to CP parameter-limited schedules. | RTO Reliability Requirement is determined through the IRM study and LDA Reliability Requirements determined through Load Deliverability analysis (CETO). - RTO Rel. Req. = Peak Load Forecast * FPR - LDA Rel. Req. = Internal Capacity + CETO The IRM study uses the 1 day in 10 years LOLE criterion and considers typical weekly/monthly peak load shapes, load uncertainty, and generation outages, etc. The CETO analysis uses a 1 day in 25 years LOLE criterion. | In the IRM study, the following uncertainties are explicity addressed: - Load uncertainty - Planned Outages - Aggregate forced outage (FO) uncertainty assuming independence in FOs of individual units (except winter peak week) - Aggregate FO uncertainty using actual aggregate data for the winter peak week | Capacity Resources (i.e. Generation, Storage, DR, EE, and/or QTUs) capable of meeting CP performance requirements. No prescriptive fuel requirements. | Cleared resources paid the RPM auction clearing price. All resources (committed or not) are eligible for Bonus Payments if performing above their expected level during Emergency Actions. Charges assessed to underperforming resources. Allowable costs included in ACR: Operations & Maintenance Labor, Administrative Expenses, Fuel Availability Expenses, Fixed Maintenance Expenses, Variable Expenses, Taxes, Fees & Insurance, Carrying Charges, Corporate Level Expenses, CP Risk, and Project Investment Recovery. Details in Tariff, Att. DD, Section 6.8.
Energy Market (DA and RT) | Commitment and dispatch of resources to meet system demand. The Energy Market consists of Day-Ahead (DA) and Real-Time (RT) markets. The Day-Ahead Market is a forward market in which hourly prices are calculated for the next operating day based on generation offers, demand bids and scheduled bilateral transactions. The Real-Time Market is a spot market in which current locational marginal prices are calculated at five-minute intervals based on actual grid operating conditions. | The objective is to minimize total system production cost and calculate LMPs that incentivize resources to follow dispatch instructions. | The Day-Ahead market runs the day before the operating day and the Real-Time market runs every five minutes during the operating day with a 10 minute look-ahead. | In the Day-Ahead market, the system is committed and dispatched to meet bid-in load and in the Real-Time market, the system is committed and dispatched to meet fixed demand. | The Day-Ahead market bid-in demand can change daily based on bid-in demand. In the RAC run, system demand is determined based on the day-ahead load forecast. In ITSCED, the two hour load forecast is used and in RTSCED, the 10 minute short-term load-forecast is used. | No uncertainties addressed in requirement. | No prescriptive fuel requirements. | Units that are committed in either the Day-Ahead or Real-Time markets are paid the LMP for the location they are dispatched at. Allowable costs include Fuel, Emissions, Variable Operating and Maintenance (costs directly related to electrical production). Details in Manual 15.
Contingency Reserves (Current) | Synchronized/Non-Synchronized Reserves provide short-term contingency response that enables the system to restore power balance following a contingency or unforeseen conditions during the operating day (i.e. after a resource loss, large tie errors, or under frequency conditions). Day-Ahead Scheduling Reserves (DASR) provide supplemental, 30-minute reserves to account for average load forecast errors and forced generator outages between the DA and RT operating horizons. | Ensure compliance with BAL-002 to recover from a major contingency loss: Recover the Area Control Error (ACE) back to it’s pre-contingency level within the allotted timeframe. | Synchronized/Non-Synchronized Reserves must respond within 10 minutes and procured with the RT Market. DASR must respond within 30 minutes and procured with the DA Market. If we have a contingency event and deploy reserves, we have 15 minutes to recover ACE and then 90 minutes after that to recover primary reserves equal to 100% of the largest contingency (105 minutes total). | NERC requirements and PJM additional requirements. Primary and Synchronized Reserve Requirements set by the ORDC. DASR Requirement based on forecasted peak load, average historical load forecasting error, and average historical forced outage rates | For Synchronized Reserves, it is equal to the size of the largest contingency plus 190 MW. For Primary Reserves, it is equal to 1.5 times the largest contingency plus 190 MW. DASR Requirement equal to Forecasted Peak Load * [Under forecasted LFE (3 yr avg) + Forced Outage Rate (3 yr avg)] | The NERC requirement is based on losing the single largest contingency in the system or zone. The likelihood of the occurrence of such event is not considered in the setting of the requirement. Uncertainty in DASR requirement includes under-forcasted LFE and FOs. | Resources capable of 30-minute response time for DASR, and resources capable of 10-minute response time for Primary and Synchronized Reserve Requirements No prescriptive fuel requirements. | Reserves are compensated at the reserve market clearing prices for the respective products (co-optimized with DA or RT Energy Markets). Allowable costs for Synch. Reserves include costs associated w/ operating a unit in condensing mode or for altering the output of a unit at the request of PJM to provide reserves.
Contingency Reserves (Price Formation Proposal) | Similar to the current Contingency Reserve Products above, but (1) aligns the DA and RT reserve products and (2) adjusts the ORDC to account for load, solar, and wind forecast errors as well as generator outages. | Ensure compliance with BAL-002 to recover from a major contingency loss: Recover the Area Control Error (ACE) back to it’s pre-contingency level within the allotted timeframe. | All reserve products procured in both DA and RT. Synchronized/Non-Synchronized Reserves must respond in 10 minutes and Secondary Reserves must respond in 30-minutes. | NERC Requirements and PJM additional requirements. Set by the ORDCs for each product, which gradually slope to $0. | NERC Requirements and PJM methodology that takes into account the real-time uncertainties in load forecast error, wind and solar forecast error and forced outages of thermal units. | The NERC requirement is based on losing the single largest contingency in the system or zone. The likelihood of the occurrence of such event is not considered in the setting of the requirement. In addition, the proposed ORDCs also capture 30-minute and 60-minute load forecast, wind forecast, solar forecast, thermal forced outages, and net interchange schedule forecast uncertainty based on the most recent 3 years of history. | Resources capable of 30-minute response time for Secondary Reserves and resources capable of 10-minute response time for Primary and Synchronized Reserve Requirements. No prescriptive fuel requirements. | Reserves are compensated at the reserve market clearing prices for the respective products (co-optimized with DA or RT Energy Markets). No change in costs.
Regulation Service | Regulation service corrects for short-term changes in electricity use that might affect the stability of the power system. It helps match generation and load and adjusts generation output to maintain the desired frequency. | Keep area control error (ACE), the difference between scheduled and actual electrical generation while accounting for variations in the system's frequency, within acceptable bounds. | Regulation procured in RT (Assignments determined 60 minutes prior to the operating hour) Resources are evaluated and scored based on their response time. PJM's performance scoring allows for a 10 second delay in response. Anything greater will receive a decreased performance score. | Requirements is 525 MW during non-ramping and 800 MW during ramping hours as stated in M12 Sec 4.4.3 Determining Regulation Assignment. | The 525/800 MW requirement was determined based on internal analysis on volatility on the system during various hours/seasons. | The requirement is based on empirical results from simulation run and administrative decisions to capture frequency deviations, load forecast errors, etc. | Resources that can respond to the Regulation Market automated signals (Reg D and Reg A) may participate. Reg D is the faster, dynamic signal that requires resources to respond almost instantaneous. Reg A is the slower signal that is meant to recover larger, longer fluctuations in system conditions. No prescriptive fuel requirements. | Resources are compensated based on a Regulation Market clearing price that is multiplied by the MWs they provide and the performance score. Reg D resources also get a mileage ratio payment on the performance credit. Generally, allowable costs include the Fuel and VOM cost increase to provide regulation, and the MarginRisk Adder.
"Resource Limited" Unit Dispatch | Generally, a unit is considered to be resource limited if it has less than 72 hours of running time at rated capacity because of resource limitations (including fuel). Participants report resource limitations to PJM for situational awareness, and during certain system conditions, PJM may request or require these units to bid in the Max Emergency category to preserve them for the times when they are needed most. | Preserve units classified as resource limited units for the times when they are needed most. | Generally, units placed in Max E when PJM declares Conservative Operations, or a Cold or Hot Weather Alert | Members notify PJM of resource limited units through Markets Gateway, as well as verbally notifying the PJM Master Coordinator at times. When PJM declares Conservative Operations or a Hot/Cold Weather Alert, resource limited units that fall below certain minimum levels are to be placed in Max Emergency, unless directed otherwise by dispatch. - CTs (onsite oil, kerosene, or diesel): < 16 hours - Steam (onsite oil or coal): < 32 hours - Gas CT/Steam units are not to be bid in as Max E for gas fuel limitations | N/A | No set requirement or uncertainties addressed in the requirement. Generally, addresses uncertainty associated with the potential inability to operate resource limited units in the upcoming days when needed if running them now. | Any "Resource Limited" unit. | No specific compensation. If PJM requests a Resource Limited unit to operate differently then what was accepted in the DA Market, then this unit would be paid its lost opportunity cost for the accepted hours that it was not run.
Maximum Generation Emergency | Emergency Procedure to increases the PJM RTO generation above the maximum economic level. It is implemented whenever generation is needed that is greater than the highest incremental cost level. PJM dispatch implements the Emergency-Bid Process, where PJM may purchases available energy from any PJM member (as emergency). | Increase the PJM RTO generation above the maximum economic level and purchase emergency energy as needed to reliably operate the system. | Alerts issued in Day-Ahead on assessment of DA Scheduling Operating Reserves. Actions issued in Real-Time; invokes operator and member action. | No set requirement. Procedure implemented as needed by dispatch. | N/A | N/A | Offers may only by designated as Max E to the extent the resource falls into one of the following categories: - Environmental limits - Fuel limits - Temporary emergency conditions at the unit - Temporary megawatt additions Dispatch may request or require "Resource Limited" units to be placed in Max E. | No specific compensation above LMP, but Emergency Bids can set LMP.
Gas/Electric Coordination | Communication and sharing of information between PJM operations and the natural gas industry for operational awareness, flexibility. Includes pipeline coordination, daily gas/electric operations analysis, and gas/electric contingency assessments. | Coordinate between electric and natural gas commitments, electric and natural gas markets, such that operators are aware of unit limitations due to fuel supply, gas infrastructure. | Daily gas/electric analysis performed in the winter. Industry days for gas are 10 AM to 10 AM, for electricity midnight to midnight. DA results posted 1:30 PM prior to gas nomination deadline 2:00 PM. | N/A | N/A | No set requirement or uncertainties addressed in the requirement. Generally, address uncertainties associated with gas/electric coordination issues. | Situational awareness focused on natural gas units and infrastructure. | N/A
Gas Contingency Procedures | Operational procedures to mitigate impact of gas contingencies on the electric system, and reflect impact of contingencies in reserves and pricing. | Mitigate impact of gas contingencies on the electric system, and reflect impact of contingencies in reserves and pricing. | RT or DA following the triggering of a gas contingency initiating event (e.g. Hot/Cold Weather, Capacity Emergency events, gas pipeline events, etc.) | No set requirement. If results of gas contingency reliability analysis show load dump violations and/or reserve deficiencies, dispatch will operate to the gas contingency (e.g. switching fuels/pipelines) and adjust reserve requirements as needed. | Use Manual language for DASR adjustment and RT adjustment Values used include the sum Eco Max for all resources defined in the contingency, and the pre-contingency reserve requirements (i.e. if Eco Max sum is > requirement, procure the difference between the two). | Potential loss of generation due to gas contingencies. | Procedures focused on natural gas units. | No specific compensation. Reserve Clearing Price (potential scheduling of/clearing of additional 30-minute or synch reserves in DA/RT if contingency merits) Recovery of switching costs for units that switch following a PJM operating instruction under discussion with stakeholders.
Transmission Planning Solution | Procedure within RTEP to determine system upgrades that provide reliability or economic benefit (i.e. reduce congestion). | Eliminate reliability issues or system constraints causing congestion. Reduce congestion costs on system. | PJM's RTEP assesses both near-term five-year needs of the regional power grid as well as those over a 15 year horizon as well. | NERC Planning Standard TPL-001-4 is applied in PJM's RTEP process through a wide range of reliability analyses, including load and generation deliverability tests. For market efficiency projects, Cost/Benefit Analysis must identify 1.25:1 Benefit/Cost ratio to be presented to the board. Upgrade construction lead times can be year(s). | For market efficiency projects, compare market simulations with and without upgrade for RTEP planning horizon. Sum benefits from energy and capacity market simulations, calculate present value. Divide this benefit by present value cost of upgrade for same period. | N/A | N/A - Transmission driven | Revenue requirement of system enhancement.
System Restoration Plan (Black Start Service) | PJM's System Restoration Plan establishes procedures for PJM and its members to restore the integrity of the interconnection as quickly as possible following a system disturbance. This includes a reliable black-start capability plan to restore power to the grid. | Establish procedures to restore the integrity of the interconnection as quickly as possible. | PJM, in collaboration with the TOs, selects Black Start units to meet Critical Load requirements during the 5 year Black Start Selection process, or as needed. | In general, must be sufficient critical Black Start units to serve critical load (plus a 10% margin) in each transmission zone, with minimum of two Black Start units for each transmission zone. | Critical load requirement for each transmission zone determined as the sum of critical cranking power load, gas infrastructure critical load and nuclear off-site station light and power load requirements, with an allowance for exceptions or additions based on unique circumstances. Required Black Start = 110% (Critical Load requirement) on a locational basis | No specific uncertainties; ensures there are committed resources to recover from blackout. | Must meet Black Start unit requirements and be selected for Black Start Service by PJM. Generally, Black Start units must maintain fuel to allow for 16 hours of run time. Fuel Assurance requirements under review in stakeholder process. | Cost Recovery Rates Revenue requirements for Black Start Service may include the following, where applicable: NERC CIP Capital Costs, fixed black start unit costs, variable black start costs, training expenses, fuel storage costs for liquefied natural gas, propane or oil and an incentive factor.
Voltage Reduction | Alert issued when the estimated operating reserve capacity is less than the forecasted synchronized reserve requirement; Warnings issued when the available synchronized reserve capacity is less than the synchronized reserve requirement. PJM issues a 5% Voltage Reduction Action when load relief is still needed to maintain tie schedules, or when needed to increase transmission system voltages. | Reduce voltage on the distribution system in order to reduce demand and therefore provide a sufficient amount of reserve to maintain tie flow schedules and preserve limited energy sources, or to increase transmission system voltages. | Alert issued 1 or more days prior to the operating day. Warnings and Actions issued during the operating day. The lead times needed to implement the voltage reduction vary by TO. | N/A | N/A | N/A | N/A | N/A
Additional Emergency Operating Procedures (e.g. Post Contingency Local Load Relief Warnings, Hot/Cold Weather Alerts, Conservative Operations, DARA, etc.) | A set of procedures on how PJM and its members are expected to respond to emergency conditions on the PJM system. | Maintain the integrity of the PJM RTO transmission systems and the Eastern Interconnection at all times. | Typically 6 days or less prior to the anticipated need (starting with Alerts). | N/A | N/A | N/A | N/A | N/A