## Setup
Enter Stakeholder Committee Name in cell A2:
Task Force: Interconnection Process Reform
Enter issue title (use title from Issue Tracking if applicable) in cell A5:

## 1. Interest Identification
Task Force: Interconnection Process Reform
Interest Identification
Instructions: List interests of all parties on this page.
Interconnection Studies:
Streamline the study process while maintaining system reliability
Align queue request windows with the study deadlines
Improve efficiency of study phases
Improve pre-application guidance and direction provided to Interconnection Customers
Improve accuracy / clarity / completeness of project information provided in applications and kick-off calls
Improve scheduling of model lockdowns and clearing of closed queues (Lockdowns covered in monthly IWG meetings)
Improve clearing of closed queues (combined with 12)
Improve modeling of system upgrades in study models - (Is this what is meant?: Improve modeling of transmission system upgrades in queue study models.)
Improve process for managing impacts across multiple TOs
Improve process for conducting combined studies
Improve accuracy of project information and process for making changes to that information prior to the start of each study phase
Improve cost estimating requirements and provide flexibility (Clarification needed)
Improve retooling criteria and address scheduling impacts
Improve identification and assignment of redispatch costs to appropriate customers (Clarification needed)
Improve modeling of deactivated generation and generation not participating in markets
Significantly reduce multi-year delays in completing facility studies
Improve developer ability to forecast study timelines, upgrade costs and construction schedules
Improve ability of transmission owners to produce realistic estimates at the system impact study phase
Improve the coordination, clarification, consistency of the deficiency review process
Ensuring stability studies are only being performed for queue projects that are actually moving forward
Improve transparency of the FaS re-tool process and the timelines associated with post TO engineering activities
Improve communications between developers and PJM in the facilities phase about changes in the timeline, re-tools and the schedule.
Improve the necessary study process to evaluate equipment modification
Replicate current affected systems study process in place between PJM / MISO and other PJM neighbors
Integrate the interconnection process with state policy resource requirements and PJM state agreement approach and a transformative grid process
Establishing methodologies for prioritizing commercially ready projects
Establish or improve cost commitments related to advancement of the study process - refundable and/or non-refundable
Establish a case review process before the actual study begins.
Establish a process for releasing cases for study before queue submission.
Define metrics for the process specifcally to time and cost
Account for multiple CIR levels within one submission
Integrate the interconnection process with state policy resource requirements and a transformative grid process
Eliminate or reduce of the ability to place generation in queue positions in suspension
Eliminate or reduce the ability to enter two or more queue positions at the same project location and time
Establish review mechanisms for generator lead lines for sight control
Introduce group studies and decision points to improve cost certainity (by removing first to cause) and reduce re-tools.
Create incentives for meeting deadlines
Shorten the time allocated ICs have to execute an ISA after receiving a completed Facility Study to reduce re-tool study time
| Create/Tighten/Enforce certainty requirements to encourage viable project queue submittals. | New
| Establish protocols for informing TO of active, withdrawn, and on-hold network upgrades. | New
| Improve transparency of the status of network upgrades | New
Cost Concerns:
Cost allocation approach to maximize throughput
Cost certainty for New Service Customers
Improve the cost allocation rule of the first project causing an overload (for example applying a minimum shift factor and/or MW impact threshold)
Improve the process so it allows for a faster, cluster based, coordinated decision making for ISA cost allocation acceptance.
Improve the security requirements for shared upgrades.
Establish methodology to socialize the costs for large upgrades.
Ensuring Network Upgrade costs are the responsibility of interconnecting generation projects.
Certanity around baseline upgrade (potential) or a network upgrade
| Improve security requirements for upgrades across multiple TO zones | New
Interim Operation and Agreements:
Ensure system reliability with interim operation studies
Improve efficiency for all parties
Minimize effect of suspension provisions on projects under study (Duplicate - Line 39)
Improve terms and conditions in Interim ISA (i.e. facilitate TO oversight for ICs that utilize the Option to Build) (tie to 68)
Improve timing of Interim ISA
Ensure projects that could pose risk to public safety or reliability of system are not placed in-service (tie to 63)
Interim ISA &/ ICSA scope needs to facilitate TO oversight for ICs that utilize the Option to Build (tie to 66)
Consistent usage of new agreements
| Improve timelines and schedules associated with construction activities | New
| Improve education on the usage of Interim ISA | New
| Improve terms/conditions for utilitzing WMPAs | New
| Improve procedures for transferring facilities in the CSA | New
New Service Request Requirements and Project Modifications:
Balance flexibility and timeliness
Reduce the amount of speculative projects
Simplify deposit structure
Higher project collateral requirements
Ability to identify company affiliates/parent companies of project developers.
Extend the Permissible Technological Advancement option after the ISA has been executed
Limit the number of technological changes allowed per project and allow the changes to be submitted within a window.
Establish appropriate interconnection security requirements for entering and progressing in the queue
Require developers to secure a certain percentage of the generator tie line and site control (Duplicate - Line 41)
Ensure entry into the queue is not overly restrictive
| Improve requirements to ensure the developer has site control and property rights earlier on in the queue process. | New
Current and Future Backlog:
Changes applied to existing and future projects
| Create/Tighten/Enforce mechanisms to cancel “stale” projects (i.e. time limits). | New
| Improve transparency of backlog by establishing public reporting requirements | New
Other:
Ensure coordination and clarity between generation energy metering and load metering
Ensure coordination and clarity between DER connecting to retail owned distribution and retail customer taking transmission service through LSE

## 1a. Categorized Interests
Task Force: Interconnection Process Reform
Interest Identification
Instructions: List interests of all parties on this page.
Application Requirements
Eliminate or reduce of the ability to place generation in queue positions in suspension
Eliminate or reduce the ability to enter two or more queue positions at the same project location and time - meant for the same queue window
Establish appropriate interconnection security requirements for entering and progressing in the queue
Establish review mechanisms for generator lead lines for sight control
Ensure entry into the queue is not overly restrictive
Improve requirements to ensure the developer has site control and property rights earlier on in the queue process.
Allow for upgrades to be included either at the same location in a new queue postion or in the existing queue position for with the project is being studied.
Incentivize earlier submission in the queue process
Incentivize fewer changes to the existing submitted queue position
Information Sharing
Improve pre-application guidance and direction provided to Interconnection Customers
Improve accuracy / clarity / completeness of project information provided in applications and kick-off calls
Improve accuracy of project information and process for making changes to that information prior to the start of each study phase
| Improve identification and assignment of redispatch costs to appropriate customers (Slide 33 AEP presentation explains reasoning) | Presentation
Improve developer ability to forecast study timelines, upgrade costs and construction schedules
Improve the coordination, clarification, consistency of the deficiency review process
Improve transparency of the FaS re-tool process and the timelines associated with post TO engineering activities
Improve communications between developers and PJM in the facilities phase about changes in the timeline, re-tools and the schedule.
Establish a process for releasing cases for study before queue submission.
Define metrics for the process specifcally to time and cost
Establish protocols for informing TO of active, withdrawn, and on-hold network upgrades.
Improve transparency of the status of network upgrades
Improve transparency of backlog by establishing public reporting requirements
Modeling
Improve modeling of system upgrades in study models - (Improve modeling of transmission system upgrades in queue study models)
Improve modeling of deactivated generation and generation not participating in markets
Minimize the use of stale interconnection models.
Better accommodate for impactful changes from the initial study parameters
Study Process
Improve scheduling of model lockdowns and clearing of closed queues (Note: Lockdowns covered in monthly IWG meetings)
Improve process for managing impacts across multiple TOs
Improve process for conducting combined studies
Improve retooling criteria and address scheduling impacts
Ensuring stability studies are only being performed for queue projects that are actually moving forward
Improve the necessary study process to evaluate equipment modification
Replicate current affected systems study process in place between PJM / MISO and other PJM neighbors
Integrate the interconnection process with state policy resource requirements and PJM state agreement approach and a transformative grid process
Establishing methodologies for prioritizing commercially ready projects
Establish a case review process before the actual study begins.
Account for multiple CIR levels within one submission
Extend the Permissible Technological Advancement option after the ISA has been executed
Improve procedures for transferring facilities in the CSA
Establish cluster study process from SIS kickoff
Make feasibility studies optional
Queue priority based on interconnection customer readiness consistent with other regions
Make feasibility study kickoff call optional
Efficiency
Streamline the study process while maintaining system reliability throughout the entire process
Align queue request windows with the study deadlines
Improve efficiency of study phases
Improve efficiency for all parties
Significantly reduce multi-year delays in completing facility studies
Introduce group studies and decision points to improve cost certainity (by removing first to cause) and reduce re-tools.
Shorten the time allocated ICs have to execute an ISA after receiving a completed Facility Study to reduce re-tool study time
Improve terms, conditions and timing of Interim ISA
Consistent usage of new agreements
Balance flexibility and timeliness
Reduce the amount of speculative projects
Limit the number of technological changes allowed per project and allow the changes to be submitted within a window
Improve timelines and schedules associated with construction activities
Improve education on the usage of Interim ISA
Improve terms/conditions for utilitzing WMPAs
Create/Tighten/Enforce mechanisms to cancel “stale” projects (i.e. time limits).
Eliminate uncertainty introduced by non-ready projects
Eliminate First to Trigger upgrade responsibility construct
Improve Order 845 interim interconnection service viability
Limit suspension rights to narrowly defined criteria including absence of downstream impacts to similarly queued projects.
Create incentives to make quicker commercial go/no go decisions on projects than
Create Fast-Track process for First-Ready for Uprates, Projects Not Requesting Additional Capacity Injection Rights (CIR) or Maximum Facility Output (MFO)First-Ready for Uprates
Costs
| Improve cost estimating requirements and provide flexibility (Slide 17 AEP presentation explains reasoning) | Presentation
Improve ability of transmission owners to produce realistic estimates at the system impact study phase
Establish or improve cost commitments related to advancement of the study process - refundable and/or non-refundable
Create incentives for meeting deadlines
Cost allocation approach to maximize throughput
Cost certainty for New Service Customers
Improve the cost allocation rule of the first project causing an overload (for example applying a minimum shift factor and/or MW impact threshold)
Improve the process so it allows for a faster, cluster based, coordinated decision making for ISA cost allocation acceptance.
Improve the security requirements for shared upgrades. (same as 88)
Establish methodology to socialize the costs for large upgrades.
Ensuring Network Upgrade costs are the responsibility of interconnecting generation projects.
Simplify deposit structure
Higher project collateral requirements
Certanity around baseline upgrade (potential) or a network upgrade
(Create/Tighten/Enforce)--> Improve certainty requirements (to encourage viable project queue submittals).
Improve security requirements for upgrades across multiple TO zones
Eliminate First to Trigger upgrade responsibility construct
Adopt cluster based cost allocation principles
More visibility into the projected reliability costs, energy deliverability, and outlet upgrade costs
Better indication on study reports of upgrade costs, maximum cost responsibility, and maximum cost exposure
Other
Changes applied to existing and future projects
Ensure coordination and clarity between generation energy metering and load metering
Ensure coordination and clarity between DER connecting to retail owned distribution and retail customer taking transmission service through LSE
Ability to identify company affiliates/parent companies of project developers

## 2. Options Matrix- Design Comp.
Task Force: Interconnection Process Reform
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A (PJM) | B | C | D | E
1 | Queue Structure |  | Priority is based on time of request, first to cause cost allocation. | Cluster/cycle based. Priority is only defined by cluster/cycle. Subsequent clusters/cycles only begin (or proceed) once milestones are reached in the prior cluster/cycle
2 | Application Queue Windows |  | Two 6 months queues annually. April 1-Sep. 30 and Oct. 1- March 31. No limit on the amount of applications accepted | Rolling until cluster/cycle closing. Closing based on completion of defined point in previous cluster/cycle
Application Requirements
3 | Application Format |  | For Generation: Attachment N - All generation requests Attachment Y - Screens process for 2 MW or less (5 MW for inverter based) requesting only energy Attachment BB - 10 kW or less | Unified application type for all generation interconnections
4 | Site Control |  | Generation site only: lease, deed, option agreement. Add resource specific information. | Generation Site only: lease, deed. Additional detail TBD
5 | Deposit |  | 1-4 months - $10K + $100/MW (Max - $110K) 5th month - $20K + $150/MW (Max - $120K) 6th month - $30K + $200/MW (Max - $130K) Refundable and (10%) non-refundable amounts Wire or check | Unified study deposit for all phases Amount - TBD Nonrefundable Amount - TBD
6 | Project Information |  | MWs requested for CIR and Energy, site plan, single line | MWs requested for CIR and Energy, site plan, single line Data including the dynamics information If state jurisdictional, the two party Interconnection Agreement with the TO/DP must be provided.
7 | Point of Interconnection |  | GPS Coordinates, address, pole number, etc. Multiple projects behind the same POI are treated as separate projects Customer may select primary or secondary POI | GPS Coordinates, address, pole number, GIS project site plan, etc. Multiple projects behind the same POI are treated as a single project Only a single Point of Interconnection will be accepted Shared Facilities agreement provided up front if behind an existing POI
8 | Requirements for a "complete" Queue Position |  | Deposit, Queue Point data, site control, signed agreement | Status Quo
9 | Deficiency Review Process |  | Will review when application receives a queue position or if no site control | Will review once the cycle closes during the application review phase
10 | PJM Deficiency Review |  | 5 business days | TBD
11 | Customer Response Period |  | 10 business days total from PJM initial determination | TBD
12 | PJM Follow up to Customer response |  | 5 business days | TBD
13 | Scoping Meeting |  | PJM to provide customer with a list of dates Customer requirement to complete based on application submission: 1-4 month - 45 days 5th month - 30 days 6th month - 20 days Can be waived by customer or held separately with customer and then with Transmission Owner | Move to a single (or few) scoping meeting(s) per TO zone.
Feasibility Study Requirements
Model Review
14 | Analytical Studies |  | DC Power Flow (Summer peak only) Short Circuit | AC Power Flow at 100% Commercial probability: Summer Peak Light Load
15 | Upgrades |  | For Primary POI only: Network Upgrade cost, scope, schedule Attachment Facilities and physical interconnecton scope, cost, and schedule Secondary POI: Sensitivity study with overloads only | Network Upgrade cost, scope, schedule Attachment Facilities and physical interconnecton scope, cost, and schedule
16 | Study window |  | November 1 - January 31 or May 1 - July 31 | 120 days from Application review phase close
Report Comment Period
17 | Interconnection Queue Models |  | Uses most recently completed RTEP case (e.g. AG1 uses 2024 RTEP) | Status Quo
18 | Study Completion Schedule |  | January 31 & July 31 | 120 days from Application review phase close
19 | Criteria for combined study |  | Small generation & no transmission violations plus TO input | TBD
System Impact Study Agreement
20 | Project Information |  | Air permit application Dynamic Data Reconfirm Attachment N data Select Primary or Secondary POI if applicable | Reconfirm initial application data Provide site control for attachment facilities
21 | Study Deposit |  | Tiered based on MW amount (Max. $300K): Greater than or equal to 20 MW - $500/MW Between 2 MW and 20 MW - $10K Less than 2 MW - $5K Refundable & (10%) Non-refundable | TBD % of Original deposit will be non-refundable
22 | Ability to waive study (*Add off ramp) |  | At discretion of Transmission Provider for Small Generation. | No ability to waive study
23 | Return Window |  | 30 calendar days from Feasibility Study issuance or the project is withdrawn | 30 calendar days from Phase 1 Study (Feas.) issuance
24 | Study process notification |  | Notice to be provided along with reason and revised due date | Cluster/cycle schedule to be posted on website
25 | Project Modifications |  | Per project modifications section outlined below | Reduction of MFO and/or CIR requested Withdrawal Equipment Changes
System Impact Study Requirements
Model Review
Kickoff Call
26 | Analytical Studies |  | AC Power flow (Summer Peak, Light Load for Coal, nuclear, wind, storage, batteries, & natural gas in some cases) Short Circuit | AC Power Flow Retool Short Circuit Study Stability Study
27 | Network Upgrades |  | Network upgrade cost, scope, schedule along with cost allocation | Network upgrade cost, scope, schedule along with cost allocation
28 | Interconnection Facilities |  | Attachment Facilties and physical interconnection scope, cost, and schedule - planning level estimate | Transmission Owner to perform Facilities Study for Interconnection Facilities
29 | Study window |  | November 1 - February 28 or May 1 - August 31 | 180 days
Report Comment Period
30 | Study Completion Schedule (*correct the the SISA reference) |  | Date specified in the System Impact Study Agreement | 180 days from the deadline for the Phase 2 agreement (SISA)
31 | Interconnection Queue Models |  | Uses most recently completed RTEP case (e.g. AG1 uses 2024 RTEP) | Status Quo
32 | Affected Systems study and coordination |  | PJM performs a high level evaluation and coordinates modeling and other information with the neighboring potentially affected system, the neighboring system responds to PJM with the outcome of any affected system requirements | Status Quo
33 | Retool Criteria |  | Projects that withdraw or modify that have potential to impact remaining projects in the queue from a cost allocation perspective | Projects will not be permitted to make changes during the study phases
34 | Study process notification |  | Notice to be provided along with reason and revised due date | Cluster/cycle schedule to be posted on website
Facilities Study Agreement
35 | Deposit |  | Tiered based on MW amount or estimated cost of 1st quarter of work, whichever is greater: Greater than or equal to 20 MW - $100K Between 2 MW and 20 MW - $50K Less than 2 MW - $15K Fully refundable | TBD % of Original deposit will be non-refundable
36 | Milestones |  | Optional based on project High-side Xfmr site control if not previously provided Site plan Others as may be required by Transmission Provider | None
37 | Cost accuracy |  | TO Zone specific and included in Schedule A if applicable | TBD |  |  |  |  | Low
38 | Ability to waive study |  | At discretion of Transmission Provider | Projects that only have interconnection facilities and no contribution to network upgrades can proceed directly to a final agreement
39 | Return Window |  | 30 calendar days from System Impact Study issuance or the project is withdrawn | 30 calendar days from Phase 2 Study (SIS) issuance
40 | Project Modifications |  | Per project modifications section outlined below | Reduction of MFO and/or CIR requested Withdrawal Equipment Changes
| Facilities Study Requirements | [7 empty] | Low - Medium
Model Review
Kickoff Call
41 | Analytical Studies |  | Dynamic / stability studies and retool analyses as needed Collective studies on retools per queue | Final Retool of Phase 2 analyses with final cost allocation Final Affected system study results |  |  |  |  | Low - High
42 | Upgrades |  | Network upgrade cost, scope, schedule Attachment Facilties and physical interconnection scope, cost, and schedule | Facilities Study by Transmission Owner for Network upgrages |  |  |  |  | Medium
43 | Study window |  | 180 days (Reasonable efforts) | 180 days |  |  |  |  | Medium - High
Report Comment Period
44 | Site Visit |  | Transmission Owner specific | None |  |  |  |  | High
45 | Scoping Meeting |  | Held at request of Interconnection Customer | None
46 | Interconnection Queue Models |  | Uses most recently completed RTEP case (e.g. AG1 uses 2024 RTEP) | Status Quo
47 | Study Completion Schedule (*remove FSA reference) |  | Date specified in the Facilities Study Agreement | 180 days from the deadline for the Phase 3 agreement (FSA)
48 | Retool Criteria |  | Projects that withdraw or modify that have potential to impact remaining projects in the queue from a cost allocation perspective | Projects will not be permitted to make changes during the study phases
49 | Sag Study (*revisit per prior conversations) |  | TO Zone specific | Not permitted as a mitigation
Project Modifications
50 | Reductions |  | Based on study phase: Before Feasibility Before SISA Before ISA | Only allowed during customer decision windows. Amounts are fixed and not studied for material modification
51 | POI Changes |  | Limited based on circumstances | Limited at decision window 1 (SISA) based on circumstances TBD
52 | Permissible Technology Advancement (*correct FSA reference) |  | Allowed before execution of FSA | Allowed before execution of FSA at a decision window
53 | Non-permissible Technology Advancement (*correct FSA reference) |  | Allowed before execution of FSA Studied for material modification within 30 calendar days | Allowed before execution of FSA at a decision window
54 | Fuel Type change |  | Studied for material modification | Not permitted
55 | Material Modification |  | Material adverse effect on the cost or timing of Interconnection Studies related to any network upgrades | Status Quo
56 | Project site move |  | Allowed as long as site control is maintained throughout the process | Permitted on adjacent parcels of land only
57 | Project Transfer |  | Allowed with a Consent to Assignment | Status Quo
58 | Withdrawals |  | Allowed at any time in the process | Only permitted during customer decision windows
Cost allocation
59 | Drivers |  | First to cause the need for the network upgrade pays 100% | Upgrades are driven by the cluster/cycle the violation is identified in
60 | Inter-queue |  | Network Upgrade cost less than or equal to $5 million: Allocated in queue identied Network Upgrade cost more than $5 million: Allocated to cost causer for 5 years after completion of network upgrade | No inter-cluster/cycle cost allocation. All contained within a cluster/cycle
61 | Thresholds (* add projects below existing thresholds) |  | Based on DFAX and MW contribution to the network upgrade | Status Quo
62 | Intersection with other system upgrades |  | Allowed if a baseline or supplemental obviates the need for a network upgrade. Those upgrades become contingent facilities. | Status Quo
Interim Interconnection Service Agreement
63 | Purpose |  | Engineering and procurement activities as agreed to between the Transmission Owner and Interconection Customer Synchronization is not permitted | Status Quo
64 | Criteria and transparency |  | TO specific evaluation using anticipated interim system conditions | TBD
65 | Name of Agreement |  | Interim Interconnection Service Agreement | Engineering and Procurement Agreement
66 | Request Time Frame |  | Any point in the study process | Can only request in Phase 3 (Facilities study phase)
Interconnection Service Agreement
67 | Issuance |  | Concurrent with the release of the Facilities Study | 60 days from the results of the Phase 3 study
68 | Execution time |  | 60 calendar days from issuance of Faciltiies Study or the project is withdrawn | 15 business days from issuance
69 | Transmission Owner execution |  | 15 business days after Interconnection Customer execution | Status Quo
70 | Necessary Study Process |  | Separate agreement along with deposit for changes to the ISA after execution at customer request | Status Quo
71 | Interim rights |  | Captured in Specifications section 2.1 | Status Quo
72 | Security Requirements |  | 100% for nondirect connection network upgrades First quarter of work for direct connection network upgrades and attachment facilities | 100% of the cost allocation that the customer is responsible for
Interconnection Construction Service Agreement
73 | Issuance |  | 45 calendar days after the execution of the ISA | 60 days from the results of the Phase 3 study
74 | Execution time |  | 90 calendar days from receipt | 15 business days from issuance
75 | Transmission Owner execution |  | 15 business days after Interconnection Customer execution | Status Quo
76 | Option to Build |  | Permitted for Direct Connection Network Upgrades and Transmission Owner Attachment Facilities if elected within 30 calendar days from receipt of Facilities Study | Permitted for Direct Connection Network Upgrades and Transmission Owner Attachment Facilities if elected during customer decision window 1 (SISA)
77 | Suspension Provisions |  | 1 year or 3 years if not material to other projects | Not permitted. Issues outside of the customer's control will be dealt with using the ISA/CSA milestones
78 | Form of Agreement |  | Separate independent three party agreement | Schedule in the ISA
Other Independent Items
79 | Overall Timeline |  | 26 months assuming no delays | 24 months
80 | Application fees supporting the process timeline |  | Fixed based on study phase | TBD
81 | TO Procedures for network upgrade and grid enhancing technologies evaluation |  | Transmission Owner specific | Status Quo
82 | Pre-application process |  | Process to provide limited information prior to entering a formal interconnection request | Remove process
83 | Incremental financial rights |  | Afforded to generation requests building network upgrades that request and meet a certain threshold | Remove ability for generation requests to receive. Previously limited to Transmission Interconnection Customers for AC/DC facilites and Merchant Network upgrades. Since first to cause is no longer a concept, this should be removed
84 | WMPA treatment |  | State interconnected projects enter the queue with everyone else and sign a WMPA which is not part of the PJM Tariff | Non jurisdictional projects must use the state's process to receive a two party interconnection agreement with the TO/DP prior to entering an interconnection application. WMPA to be incorporated into the PJM Tariff
Interim Deliverability
85 | Cost |  | Included in existing study deposits | Status Quo
86 | Schedule transparency |  | Results available prior to each auction | Schedule to be posted on website
Reporting Requirements
87 | Reason for delays, suspensions, and timeline (* will need to schedule deadline delays similar to other RTO's) |  | PJM required to report to FERC if two consecutive reporting periods exceed the 25% performance threshold outlined in Section 41 of the OATT on a per study phase basis. Suspension timing not publicly available | Status Quo
88 | Timely communication, transparency, documentation on affected systems, issues and studies |  | Outlined in each regional coordination agreement | Status Quo
Dispute Resolution
89 | Informal Dispute Resolution |  | Per Section 12.1 of OATT | Status Quo
90 | File Unexecuted |  | Interconnection Customer or Transmission Owner may request to have the agreement filed unexecuted with the commission | Status Quo

## 2a. Design Component Details
Task Force: Interconnection Process Reform
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
Task Force: Interconnection Process Reform
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
Task Force: Interconnection Process Reform
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1
2
3
4
5
6
7
8
9 | [8 empty] | Low
10 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
Task Force: Interconnection Process Reform
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
Task Force: Interconnection Process Reform
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
Task Force: Interconnection Process Reform
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3