## Setup
Enter Stakeholder Committee Name in cell A2:
Task Force: Interconnection Process Reform
Enter issue title (use title from Issue Tracking if applicable) in cell A5:

## 1. Interest Identification
Task Force: Interconnection Process Reform
Interest Identification
Instructions: List interests of all parties on this page.
Interconnection Studies:
Streamline the study process while maintaining system reliability
Align queue request windows with the study deadlines
Improve efficiency of study phases
Improve pre-application guidance and direction provided to Interconnection Customers
Improve accuracy / clarity / completeness of project information provided in applications and kick-off calls
Improve scheduling of model lockdowns and clearing of closed queues (Lockdowns covered in monthly IWG meetings)
Improve clearing of closed queues (combined with 12)
Improve modeling of system upgrades in study models - (Is this what is meant?: Improve modeling of transmission system upgrades in queue study models.)
Improve process for managing impacts across multiple TOs
Improve process for conducting combined studies
Improve accuracy of project information and process for making changes to that information prior to the start of each study phase
Improve cost estimating requirements and provide flexibility (Clarification needed)
Improve retooling criteria and address scheduling impacts
Improve identification and assignment of redispatch costs to appropriate customers (Clarification needed)
Improve modeling of deactivated generation and generation not participating in markets
Significantly reduce multi-year delays in completing facility studies
Improve developer ability to forecast study timelines, upgrade costs and construction schedules
Improve ability of transmission owners to produce realistic estimates at the system impact study phase
Improve the coordination, clarification, consistency of the deficiency review process
Ensuring stability studies are only being performed for queue projects that are actually moving forward
Improve transparency of the FaS re-tool process and the timelines associated with post TO engineering activities
Improve communications between developers and PJM in the facilities phase about changes in the timeline, re-tools and the schedule.
Improve the necessary study process to evaluate equipment modification
Replicate current affected systems study process in place between PJM / MISO and other PJM neighbors
Integrate the interconnection process with state policy resource requirements and PJM state agreement approach and a transformative grid process
Establishing methodologies for prioritizing commercially ready projects
Establish or improve cost commitments related to advancement of the study process - refundable and/or non-refundable
Establish a case review process before the actual study begins.
Establish a process for releasing cases for study before queue submission.
Define metrics for the process specifcally to time and cost
Account for multiple CIR levels within one submission
Integrate the interconnection process with state policy resource requirements and a transformative grid process
Eliminate or reduce of the ability to place generation in queue positions in suspension
Eliminate or reduce the ability to enter two or more queue positions at the same project location and time
Establish review mechanisms for generator lead lines for sight control
Introduce group studies and decision points to improve cost certainity (by removing first to cause) and reduce re-tools.
Create incentives for meeting deadlines
Shorten the time allocated ICs have to execute an ISA after receiving a completed Facility Study to reduce re-tool study time
| Create/Tighten/Enforce certainty requirements to encourage viable project queue submittals. | New
| Establish protocols for informing TO of active, withdrawn, and on-hold network upgrades. | New
| Improve transparency of the status of network upgrades | New
Cost Concerns:
Cost allocation approach to maximize throughput
Cost certainty for New Service Customers
Improve the cost allocation rule of the first project causing an overload (for example applying a minimum shift factor and/or MW impact threshold)
Improve the process so it allows for a faster, cluster based, coordinated decision making for ISA cost allocation acceptance.
Improve the security requirements for shared upgrades.
Establish methodology to socialize the costs for large upgrades.
Ensuring Network Upgrade costs are the responsibility of interconnecting generation projects.
Certanity around baseline upgrade (potential) or a network upgrade
| Improve security requirements for upgrades across multiple TO zones | New
Interim Operation and Agreements:
Ensure system reliability with interim operation studies
Improve efficiency for all parties
Minimize effect of suspension provisions on projects under study (Duplicate - Line 39)
Improve terms and conditions in Interim ISA (i.e. facilitate TO oversight for ICs that utilize the Option to Build) (tie to 68)
Improve timing of Interim ISA
Ensure projects that could pose risk to public safety or reliability of system are not placed in-service (tie to 63)
Interim ISA &/ ICSA scope needs to facilitate TO oversight for ICs that utilize the Option to Build (tie to 66)
Consistent usage of new agreements
| Improve timelines and schedules associated with construction activities | New
| Improve education on the usage of Interim ISA | New
| Improve terms/conditions for utilitzing WMPAs | New
| Improve procedures for transferring facilities in the CSA | New
New Service Request Requirements and Project Modifications:
Balance flexibility and timeliness
Reduce the amount of speculative projects
Simplify deposit structure
Higher project collateral requirements
Ability to identify company affiliates/parent companies of project developers.
Extend the Permissible Technological Advancement option after the ISA has been executed
Limit the number of technological changes allowed per project and allow the changes to be submitted within a window.
Establish appropriate interconnection security requirements for entering and progressing in the queue
Require developers to secure a certain percentage of the generator tie line and site control (Duplicate - Line 41)
Ensure entry into the queue is not overly restrictive
| Improve requirements to ensure the developer has site control and property rights earlier on in the queue process. | New
Current and Future Backlog:
Changes applied to existing and future projects
| Create/Tighten/Enforce mechanisms to cancel “stale” projects (i.e. time limits). | New
| Improve transparency of backlog by establishing public reporting requirements | New
Other:
Ensure coordination and clarity between generation energy metering and load metering
Ensure coordination and clarity between DER connecting to retail owned distribution and retail customer taking transmission service through LSE

## 1a. Categorized Interests
Task Force: Interconnection Process Reform
Interest Identification
Instructions: List interests of all parties on this page.
Application Requirements
Eliminate or reduce of the ability to place generation in queue positions in suspension
Eliminate or reduce the ability to enter two or more queue positions at the same project location and time - meant for the same queue window
Establish appropriate interconnection security requirements for entering and progressing in the queue
Establish review mechanisms for generator lead lines for sight control
Ensure entry into the queue is not overly restrictive
Improve requirements to ensure the developer has site control and property rights earlier on in the queue process.
Allow for upgrades to be included either at the same location in a new queue postion or in the existing queue position for with the project is being studied.
Incentivize earlier submission in the queue process
Incentivize fewer changes to the existing submitted queue position
Information Sharing
Improve pre-application guidance and direction provided to Interconnection Customers
Improve accuracy / clarity / completeness of project information provided in applications and kick-off calls
Improve accuracy of project information and process for making changes to that information prior to the start of each study phase
| Improve identification and assignment of redispatch costs to appropriate customers (Slide 33 AEP presentation explains reasoning) | Presentation
Improve developer ability to forecast study timelines, upgrade costs and construction schedules
Improve the coordination, clarification, consistency of the deficiency review process
Improve transparency of the FaS re-tool process and the timelines associated with post TO engineering activities
Improve communications between developers and PJM in the facilities phase about changes in the timeline, re-tools and the schedule.
Establish a process for releasing cases for study before queue submission.
Define metrics for the process specifcally to time and cost
Establish protocols for informing TO of active, withdrawn, and on-hold network upgrades.
Improve transparency of the status of network upgrades
Improve transparency of backlog by establishing public reporting requirements
Modeling
Improve modeling of system upgrades in study models - (Improve modeling of transmission system upgrades in queue study models)
Improve modeling of deactivated generation and generation not participating in markets
Minimize the use of stale interconnection models.
Better accommodate for impactful changes from the initial study parameters
Study Process
Improve scheduling of model lockdowns and clearing of closed queues (Note: Lockdowns covered in monthly IWG meetings)
Improve process for managing impacts across multiple TOs
Improve process for conducting combined studies
Improve retooling criteria and address scheduling impacts
Ensuring stability studies are only being performed for queue projects that are actually moving forward
Improve the necessary study process to evaluate equipment modification
Replicate current affected systems study process in place between PJM / MISO and other PJM neighbors
Integrate the interconnection process with state policy resource requirements and PJM state agreement approach and a transformative grid process
Establishing methodologies for prioritizing commercially ready projects
Establish a case review process before the actual study begins.
Account for multiple CIR levels within one submission
Extend the Permissible Technological Advancement option after the ISA has been executed
Improve procedures for transferring facilities in the CSA
Establish cluster study process from SIS kickoff
Make feasibility studies optional
Queue priority based on interconnection customer readiness consistent with other regions
Make feasibility study kickoff call optional
Efficiency
Streamline the study process while maintaining system reliability throughout the entire process
Align queue request windows with the study deadlines
Improve efficiency of study phases
Improve efficiency for all parties
Significantly reduce multi-year delays in completing facility studies
Introduce group studies and decision points to improve cost certainity (by removing first to cause) and reduce re-tools.
Shorten the time allocated ICs have to execute an ISA after receiving a completed Facility Study to reduce re-tool study time
Improve terms, conditions and timing of Interim ISA
Consistent usage of new agreements
Balance flexibility and timeliness
Reduce the amount of speculative projects
Limit the number of technological changes allowed per project and allow the changes to be submitted within a window
Improve timelines and schedules associated with construction activities
Improve education on the usage of Interim ISA
Improve terms/conditions for utilitzing WMPAs
Create/Tighten/Enforce mechanisms to cancel “stale” projects (i.e. time limits).
Eliminate uncertainty introduced by non-ready projects
Eliminate First to Trigger upgrade responsibility construct
Improve Order 845 interim interconnection service viability
Limit suspension rights to narrowly defined criteria including absence of downstream impacts to similarly queued projects.
Create incentives to make quicker commercial go/no go decisions on projects than
Create Fast-Track process for First-Ready for Uprates, Projects Not Requesting Additional Capacity Injection Rights (CIR) or Maximum Facility Output (MFO)First-Ready for Uprates
Costs
| Improve cost estimating requirements and provide flexibility (Slide 17 AEP presentation explains reasoning) | Presentation
Improve ability of transmission owners to produce realistic estimates at the system impact study phase
Establish or improve cost commitments related to advancement of the study process - refundable and/or non-refundable
Create incentives for meeting deadlines
Cost allocation approach to maximize throughput
Cost certainty for New Service Customers
Improve the cost allocation rule of the first project causing an overload (for example applying a minimum shift factor and/or MW impact threshold)
Improve the process so it allows for a faster, cluster based, coordinated decision making for ISA cost allocation acceptance.
Improve the security requirements for shared upgrades. (same as 88)
Establish methodology to socialize the costs for large upgrades.
Ensuring Network Upgrade costs are the responsibility of interconnecting generation projects.
Simplify deposit structure
Higher project collateral requirements
Certanity around baseline upgrade (potential) or a network upgrade
(Create/Tighten/Enforce)--> Improve certainty requirements (to encourage viable project queue submittals).
Improve security requirements for upgrades across multiple TO zones
Eliminate First to Trigger upgrade responsibility construct
Adopt cluster based cost allocation principles
More visibility into the projected reliability costs, energy deliverability, and outlet upgrade costs
Better indication on study reports of upgrade costs, maximum cost responsibility, and maximum cost exposure
Other
Changes applied to existing and future projects
Ensure coordination and clarity between generation energy metering and load metering
Ensure coordination and clarity between DER connecting to retail owned distribution and retail customer taking transmission service through LSE
Ability to identify company affiliates/parent companies of project developers

## 2. Options Matrix- Design Comp.
Task Force: Interconnection Process Reform
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A (PJM) | B (Geenex) | C (Clearway) | D | E
1 | Queue Structure |  | Priority is based on time of request, first to cause cost allocation. | Cycle based converting from a First come - First Serve process to a First Ready - First Serve process. Priority is only defined by cycle. Phase 1 of the subsequent cycle only begins (or proceeds) once Phase 3 of the previous cycle and the application review period concludes. | One (1) queue cluster/cycle per calendar year. If there is retroactive queue clustering, then queue cluster AG2 should be an independent queue cluster and not combined with AH1 and AH2 queues. | Agree with PJM proposal. Miletone dates should be mandated to ensure timeline certainty
2 | Application Queue Windows |  | Two 6 months queues annually. April 1-Sep. 30 and Oct. 1- March 31. No limit on the amount of applications accepted | Rolling until cycle application deadline. Application deadline posted on conclusion of Phase #2 of previous cycle (120 days in advance). | One (1) queue cluster/cycle per calendar year. AH1 & AH2 study processes should not be started until AG2 queue projects receive their SIS Report. | Suggest two open queue windows annually. Milestone dates should be mandated to ensure timeline certainty
3 | Cycle Definition |  | N/A | All valid applications received between application deadlines.
Application Requirements
4 | Application Format |  | For Generation: Attachment N - All generation requests Attachment Y - Screens process for 2 MW or less (5 MW for inverter based) requesting only energy Attachment BB - 10 kW or less | Unified application type for all generation interconnections. |  | Have a clear interconnection request template - avoid deficiency notices after application submission. Interconnection request portal needs to allow for numerous interconnection requests and one that allows for draft requests to be saved and revisted prior to final submittal
5 | Site Control |  | Generation site only: lease, deed, option agreement. Add resource specific information. | Generation Site only: lease, deed, option agreement. Resource specific acreage requirements to be provided. |  | $500,000 Security in lieu of site control for entrance into Phase 1. Demonstration of site exclusivity prior to entrance of Phase 2 - release of security. If demonstration of site control isn't made prior to Phase 2, queue position is withdrawn and $250,000 of security is liquidated, remainder $250,000 is released to Interconnection Customer
6 | Deposit |  | 1-4 months - $10K + $100/MW (Max - $110K) 5th month - $20K + $150/MW (Max - $120K) 6th month - $30K + $200/MW (Max - $130K) Refundable and (10%) non-refundable amounts Wire or check | Unified refundable study deposit for all phases Amount - scaling based on the MW size of the project as follows: 0 - 20 MW - $75,000 >20 MW - 50 MW - $200,000 >50 MW - 100 MW - $250,000 >100 MW - 250 MW - $300,000 >250 MW - 750 MW - $350,000 >750 MW - $400,000 Readiness Payment 1 (RP1) - scaled based on MW size at $4,000 / MW (50% at risk if withdrawn by IC D1) | Readiness Payment 1 (RP1) = $4,000/MW with a $500k cap per queue project. RP1 should be at least 75% refundable initially. | TBD not against unified study deposit - clarify whether unified study deposit is for schedule, or MW; need to know more detailed $ Clarify if Deposit is used for the interconnection study or if it is used for withdrawl penalty.
7 | Project Information |  | MWs requested for CIR and Energy, site plan, single line | MWs requested for CIR and Energy, site plan, single line Data including the dynamics information If state jurisdictional, the two party Interconnection Agreement with the TO/DP must be provided. Any claiming of CIRs from deactivating units must be concurrent with the application. | Gas plants need to provide information about what pipeline upgrades may be necessary to accommodate their plant. If CIRs are being used from retiring plant by an interconnection customer, that should be made public prior to the start of Phase 1. Describe how the allocation of network upgrades are adjusted if an interconnection customer claims CIRs from a retiring plant. | No objection to PJM proposal
8 | Point of Interconnection |  | GPS Coordinates, address, pole number, etc. Multiple projects behind the same POI are treated as separate projects Customer may select primary or secondary POI | GPS Coordinates, address, pole number, GIS project site plan, etc. Multiple projects behind the same POI are treated as a single project Only a single Point of Interconnection will be accepted Shared Facilities agreement provided up front if behind an existing POI | Single Point of Interconnection is reasonable. | -Studying two projects at the same POI should be retained and if submitted as two unique interconnection requests should result in two descrete GIAs - New requests behind an existing POI should require a consent agreement prior to Phase 1. Draft Shared Facilities Agreement prior to GIA execution
9 | Requirements for a "complete" Queue Position |  | Deposit, Queue Point data, site control, signed agreement | Status Quo |  | No objection to PJM proposal
10 | Deficiency Review Process |  | Will review when application receives a queue position or if no site control | Will review once the cycle closes during the application review phase. There will be no reviews prior to the application deadline. |  | Initiate application review once request is submitted during open queue window - encourages early entry to address deficiencies. Recommend deposit in lieu of site control
11 | PJM Deficiency Review |  | 5 business days | 15 business days |  | Status quo
12 | Customer Response Period |  | 10 business days total from PJM initial determination | 10 business days total from PJM initial determination |  | Status quo
13 | PJM Follow up to Customer response |  | 5 business days | 15 business days |  | Status quo
14 | Scoping Meeting |  | PJM to provide customer with a list of dates Customer requirement to complete based on application submission: 1-4 month - 45 days 5th month - 30 days 6th month - 20 days Can be waived by customer or held separately with customer and then with Transmission Owner | Move to a single (or few) scoping meeting(s) per TO zone. Flexible as to the number of projects and customer/TO preference. To be completed during the Application Review phase. May be waived by customer | Transmission Owners to provide more up to date maps that Interconnection Customers can access and/or identify a specific TO representative that would be responsible for answering IC questions about their assets in a timely manner. | Provide a single scoping meeting per TO zone to communicate to all ICs what the queue looks like and what known constraints are in the area to encourage IRs to withdraw if the area is overly constrained. Give the option to ICs to request a project specific scoping mtg prior to start of the cluster
15 | Application Review Time Period |  | No defined period. | 90 days or the amount of time it takes to complete all Application review activities, whichever is greater | 60 days along with a 30 deficiency cure period.
16 | Parent Company Information |  | Not Required | Required on Application
| Feasibility Study Requirements |  |  | Phase 1
| Model Review |  | No model review period. | Model to be posted to CEII protected portion of PJM website
16 | Analytical Studies |  | DC Power Flow (Summer peak only) Short Circuit | AC Power Flow at 100% Commercial probability: Summer Peak Light Load |  | Eliminate Feasibility Study - move to Phase 1 definitive study methodology focused on AC load flow analysis and short circuit study. Early identification of Affected Systems
17 | Upgrades |  | For Primary POI only: Network Upgrade cost, scope, schedule Attachment Facilities and physical interconnecton scope, cost, and schedule Secondary POI: Sensitivity study with overloads only | Network Upgrade cost, scope, schedule, & cost allocation Attachment Facilities and physical interconnecton scope, cost, and schedule | Potential impact to Affected Systems should also be identified. | Phase 1 upgrades should identify maximum cost cap responsibility for interconnection customers and should inform the posting requirements to advance into Phase 2. All DA upgrade postings should be fully refundable and all shared facility upgrades should have a portion retained as non-refundable once the project advances into subsequent study phases
18 | Study window |  | November 1 - January 31 or May 1 - July 31 | 120 days from Application review phase close |  | No objection - maintain two open queue cycles per year
| Report Comment Period |  | Concurrent with the time to return the SISA | Concurrent with Interconnection Customer Decision 1 | PJM should be obligated to revise their studies if the comment period surfaces inaccuracies.
19 | Interconnection Queue Models |  | Uses most recently completed RTEP case (e.g. AG1 uses 2024 RTEP) | Status Quo | If there is a new overload identified in the RTEP case, cost for such overload should not be assigned to Interconnection Customers. | Consolidated planning model should be used for generation interconnection studies
20 | Study Completion Schedule |  | January 31 & July 31 | 120 days from Application review phase close |  | No objection to PJM proposal
21 | Criteria for combined study |  | Small generation & no transmission violations plus TO input | Phase 1 study is already a System Impact Study from a load flow perspective.
| System Impact Study Agreement |  |  | Interconnection Customer Decision 1
22 | Project Information |  | Air permit application Dynamic Data Reconfirm Attachment N data Select Primary or Secondary POI if applicable | Reconfirm initial application data Provide site control for customer interconnection facilities and interconnection switchyard (if applicable) Provide evidence of air & water permits (if applicable) | Gas plants need to provide information about what pipeline upgrades may be necessary to accommodate their plant. | Demonstration of site control prior to Phase 2 entance - release of deposit in lieu of site control
23 | Study Deposit |  | Tiered based on MW amount (Max. $300K): Greater than or equal to 20 MW - $500/MW Between 2 MW and 20 MW - $10K Less than 2 MW - $5K Refundable & (10%) Non-refundable | 10% of Network Upgrade costs as Readiness Payment 2 (RP2) 100% of RP1 is at risk | Readiness Payment 2 (RP2) - RP2 should be at least 75% refundable initially. | Study deposit should only be used to complete the engineering and study work for each interconnection request. A separate posting based on DA and shared facilities identified in the Phase 1 study report should be the basis for Phase 2 entrance and a portion of the shared upgrade posting should be deemed non-refundable
24 | Ability to waive study (Off-ramp) |  | At discretion of Transmission Provider for Small Generation. | Off-ramp - Projects that do not contribute to the need for network upgrades and do not require a Facilities Study for their Interconnection Facilities may proceed to a Final Agreement |  | No objection to PJM proposal
25 | Return Window |  | 30 calendar days from Feasibility Study issuance or the project is withdrawn | 30 calendar days from Phase 1 Study issuance |  | 10 BD cure period after defincieny notice has been provided to IC
26 | Study process notification |  | Notice to be provided along with reason and revised due date | Cycle schedule to be posted on website along with reasons for any delays |  | Send email notifications when schedules are updated.
27 | Project Modifications |  | Per project modifications section outlined below | Reduction of MFO and/or CIRs requested up to 100% Withdrawal Equipment Changes |  | Unconstricted MFO and/or CIR reductions should be allowed prior to Phase 2 entance. Equipment changes should be allowed as long as no material impact.
| System Impact Study Requirements |  |  | Phase 2
28 | Model Review |  | No model review period. | Model to be posted to CEII protected portion of PJM website
29 | Kickoff Call |  | No kick-off call | N/A - no requirement but can be held at the request of the Transmission Owner or customer
30 | Analytical Studies |  | AC Power flow (Summer Peak, Light Load for Coal, nuclear, wind, storage, batteries, & natural gas in some cases) Short Circuit | AC Power Flow Retool Short Circuit Study Stability Study |  | No objection to PJM proposal
31 | Network Upgrades |  | Network upgrade cost, scope, schedule along with cost allocation | Network upgrade cost, scope, schedule along with cost allocation |  | Maximum cost cap is adjusted to the minimum of Phase 1 or Phase 2 cost allocated shared network upgrade. Upgrade schedule for identified NUs should be binding to provide IC timing certainty
32 | Interconnection Facilities |  | Attachment Facilties and physical interconnection scope, cost, and schedule - planning level estimate | Transmission Owner to perform Facilities Study for Interconnection Facilities |  | IF cost and schedule should be binding to provide IC cost and timing certainty
33 | Study window |  | November 1 - February 28 or May 1 - August 31 | 180 days |  | 150 days
| Report Comment Period |  | Concurrent with the return of the Facilities Study Agreement | Concurrent with Interconnection Customer Decision 2
34 | Study Completion Schedule |  | Date specified in the System Impact Study Agreement | 180 days from the deadline for the Interconnection Customer Decision 1 |  | No objection to PJM proposal
35 | Interconnection Queue Models |  | Uses most recently completed RTEP case (e.g. AG1 uses 2024 RTEP) | Status Quo | If there is a new overload identified in the RTEP case, cost for such overload should not be assigned to Interconnection Customers. | Consolidated planning model should be used for generation interconnection studies
36 | Affected Systems study and coordination |  | PJM performs a high level evaluation and coordinates modeling and other information with the neighboring potentially affected system, the neighboring system responds to PJM with the outcome of any affected system requirements | Status Quo | Affected Systems Studies need to be sequenced. Phase 1 - PJM should have indication of potential impact of Affected Systems by the end of Phase 1 study. Phase 2 - PJM should be able to confirm that there is an impact from Affected System owner by the end of Phase 2 along with a cost estimate/schedule if work is identified. Phase 3 - Affected System Study Report finalized. PJM need to provide more information on its website as to which queue projects are being delayed by Affected Systems issues along with which Affected System/TO is responsible. PJM and other ISO/RTOs (MISO, NYISO, DEP and others) need to better align their queue study cycles and timelines in order to more effective handle Affected Systems issues. | Identification of Affected Systems needs to occur during scoping meeting and Phase 1 study. Need to put in a timeline for completion of Affected System study. Queue reform needs to address coordinated planning process with affected systems
37 | Retool Criteria |  | Projects that withdraw or modify that have potential to impact remaining projects in the queue from a cost allocation perspective | Projects will not be permitted to make changes during the study phases |  | Modifications after the Phase 2 study phase should be evaluated under a Material Modification Assessment process with clear guidelines on what modifications are allowed through the confirmation process
38 | Study process notification |  | Notice to be provided along with reason and revised due date | Cycle schedule to be posted on website along with reasons for any delays |  | Should have a scoping call to let customers know the detailed scope and study groups.
| Facilities Study Agreement |  |  | Interconnection Customer Decision 2
39 | Deposit |  | Tiered based on MW amount or estimated cost of 1st quarter of work, whichever is greater: Greater than or equal to 20 MW - $100K Between 2 MW and 20 MW - $50K Less than 2 MW - $15K Fully refundable | 20% of Network Upgrade costs as Readiness Payment 3 (RP3) RP3 is 100% at risk | Readiness Payment 3 (RP3) - RP3 should be at least 75% refundable initially. | Facility study should be replaced with Phase 3 study process. Allows for final retooling of the SIS and finalization of the upgrade scope and cost / schedule
40 | Milestones |  | Optional based on project High-side Xfmr site control if not previously provided Site plan Others as may be required by Transmission Provider | None | Execution of Affected System Study Agreements if necessary.
41 | Cost accuracy |  | TO Zone specific and included in Schedule A if applicable | TO Zone specific |  | IF cost and schedule should be binding to provide IC cost and timing certainty |  |  | Low
42 | Ability to waive study (Off-ramp) |  | At discretion of Transmission Provider | Off-ramp - Projects that only have interconnection facilities and no contribution to network upgrades can proceed directly to a final agreement |  | No objection to PJM proposal
43 | Return Window |  | 30 calendar days from System Impact Study issuance or the project is withdrawn | 30 calendar days from Phase 2 Study issuance |  | 10 BD cure period after defincieny notice has been provided to IC
44 | Project Modifications |  | Per project modifications section outlined below | Reduction of MFO and/or CIR requested of 10% of what was studied during Phase 2 Withdrawal Equipment Changes under permissible technology advancements |  | Modifications after the Phase 3 study phase should be evaluated under a Material Modification Assessment process with clear guidelines on what modifications are allowed through the confirmation process
| Facilities Study Requirements |  |  | Phase 3 |  |  |  |  | Low - Medium
45 | Model Review |  | No model review period. | Model to be posted to CEII protected portion of PJM website
46 | Kickoff Call |  | Held to discuss specifics for the Interconnection Facilities | N/A - kick-off call is not necessary for network upgrades | Add kickoff call with Affected System owner if Affected System Study Agreement is necessary. Call is needed to review specifics for Interconnection Facilities. Including which power flow models are used for tie-lines and non-tie lines in the study.
47 | Analytical Studies |  | Dynamic / stability studies and retool analyses as needed Collective studies on retools per queue | Final Retool of Phase 2 analyses with final cost allocation Final Affected system study results |  | Dynamic stability and voltage study should be done at system impact study phase. |  |  | Low - High
48 | Upgrades |  | Network upgrade cost, scope, schedule Attachment Facilties and physical interconnection scope, cost, and schedule | Facilities Study by Transmission Owner for Network upgrades |  | Any indentified upgrades are subject to the cost cap provided to the IC throughout the study process |  |  | Medium
49 | Study window |  | 180 days (Reasonable efforts) | 180 days |  | 90 days |  |  | Medium - High
| Report Comment Period |  | Concurrent with the ISA execution period. | Concurrent with Interconnection Customer Decision 3
50 | Site Visit |  | Transmission Owner specific | None |  | No objection to PJM proposal |  |  | High
51 | Scoping Meeting |  | Held at request of Interconnection Customer | None |  | status quo
52 | Interconnection Queue Models |  | Uses most recently completed RTEP case (e.g. AG1 uses 2024 RTEP) | Status Quo | If there is a new overload identified in the RTEP case, cost for such overload should not be assigned to Interconnection Customers. | Consolidated planning model should be used for generation interconnection studies
53 | Study Completion Schedule |  | Date specified in the Facilities Study Agreement | 180 days from the deadline for the Interconnection Customer Decision 2 |  | 95 days (Phase 1, Phase 2, Phase 3 = 365 days)
54 | Retool Criteria |  | Projects that withdraw or modify that have potential to impact remaining projects in the queue from a cost allocation perspective | Projects will not be permitted to make changes during the study phases |  | Modifications after the Phase 3 study phase should be evaluated under a Material Modification Assessment process with clear guidelines on what modifications are allowed through the confirmation process
55 | Sag Study |  | TO Zone specific | Not permitted as a network upgrade but may be performed in Phase 2 in order to determine full scope of network upgrade required.
Interconnection Customer Decision 3
56 | Deposit |  | None | Customer to post their portion of the security required in order to proceed to a final agreement | Posted security should be refundable for large cost increases (i.e. Sag studies results can indicate significant network upgrade costs).
57 | Project Information |  | None | Customer to provide site control for generating site, customer interconnection facilities, and interconnection switchyard (if applicable) Customer to provide evidence of necessary state, county, & local permits or a milestone will be created in the final agreement | If necessary, gas plants need to provide evidence that plans for needed pipeline upgrades have been initiated. Gas plants to confirm that application were submitted for Title V permits.
Project Modifications
58 | Reductions |  | Based on study phase: Before Feasibility Before SISA Before ISA | Only allowed during customer decision windows. Amounts are fixed and not studied for material modification |  | Provide flexibility of reducing MW size at various stages subject to material modification assessment. If size change is deemed material the IC can withdraw the change request and keep interconnection request valid
59 | POI Changes |  | Limited based on circumstances | Limited at Interconnection Customer Decision 1 based on circumstances to be further outlined |  | Changes allowed prior to Phase 2 study subject to confirming no material impact to Phase 1 shared upgrades
60 | Permissible Technology Advancement |  | Allowed before execution of FSA | Allowed before the start of Phase 3 at either Interconnection Decision 1 or 2 |  | Allowed at any time subject to MMA
61 | Non-permissible Technology Advancement |  | Allowed before execution of FSA Studied for material modification within 30 calendar days | Allowed before the start of Phase 3 at either Interconnection Decision 1 or 2 |  | Allowed at any time subject to MMA
62 | Fuel Type change |  | Studied for material modification | Not permitted |  | Single Fuel: Wind/solar -> battery, vice versa. Similarly,would like to have some flexibility - at a minimum, want it to be studied for material modification. Mixed Fuel: Wind + battery, solar + battery --> maintain the same capacity (interconnection service level), allow flexibility to adjust MW sizes among the technology - prior to certain interconnection milestones; still evaluate them for material modifications. Pre-wire a path for fast tracking the evaluation. Allow customers to submit our own evaluations to support PJM's fast-track evaluations. Establish what automatically consitutes materials.
63 | Material Modification |  | Material adverse effect on the cost or timing of Interconnection Studies related to any network upgrades | Status Quo |  | Specify specific changes that are allowed to be evaluated by a MMA.
64 | Project site move |  | Allowed as long as site control is maintained throughout the process | Permitted on adjacent parcels of land only where site control has previously been provided with the application |  | Status quo after Phase 2 and so long as the POI does not change unless otherwise approved via MMA
65 | Project Transfer |  | Allowed with a Consent to Assignment | Status Quo |  | No objection
66 | Withdrawals |  | Allowed at any time in the process | Only permitted during customer decision windows |  | Status quo - interconnection customers should be able to withdraw at any time
Cost allocation
67 | Drivers |  | First to cause the need for the network upgrade pays 100% | Upgrades are driven by the cycle the violation is identified in |  | Upgrades are identified and cost allocated by resource shift factors and contributions to overloads. Shift factor levels for cost allocation should be discussed by stakeholders based on the study methodology being deployed (reliability vs. deliverability contingencies) Network upgrades are subject to rate recovery and reimbursements to interconnection customers up to a defined $/MW
68 | Inter-queue |  | Network Upgrade cost less than or equal to $5 million: Allocated in queue identied Network Upgrade cost more than $5 million: Allocated to cost causer for 5 years after completion of network upgrade | No inter-cycle cost allocation. All contained within a cycle |  | Please clarify - does this mean later queued projects would not be cost allocated for prior-queue projects upgrades?
69 | Thresholds |  | Based on DFAX and MW contribution to the network upgrade for those first to cause and higher (100% and above) | Based on DFAX and MW contribution to the network upgrade for all projects |  | Upgrades are identified and cost allocated by resource shift factors and contributions to overloads. Shift factor levels for cost allocation should be discussed by stakeholders based on the study methodology being deployed (reliability vs. deliverability contingencies)
70 | Intersection with other system upgrades |  | Allowed if a baseline or supplemental obviates the need for a network upgrade. Those upgrades become contingent facilities. | Status Quo |  | Any identified Cluster Study Network upgrade should be evaluated as a possible baseline or policy driven upgrade to be approved through the related planning process and funded through these processess
Interim Interconnection Service Agreement
71 | Purpose |  | Engineering and procurement activities as agreed to between the Transmission Owner and Interconection Customer Synchronization is not permitted | Status Quo |  | Allowed after Phase 2 study results
72 | Criteria and transparency |  | TO specific evaluation using anticipated interim system conditions | Status Quo
73 | Name of Agreement |  | Interim Interconnection Service Agreement | Engineering and Procurement Agreement
74 | Request Time Frame |  | Any point in the study process | Can only request in Phase 3 |  | Allowed after Phase 2 study results
Interconnection Service Agreement
75 | Issuance |  | Concurrent with the release of the Facilities Study | 60 days from the results of the Phase 3 study |  | Tender draft ISA at the time of the Phase 3 study report
76 | Execution time |  | 60 calendar days from issuance of Faciltiies Study or the project is withdrawn | 15 business days from issuance |  | 90 days for good faith negotiation and execution. Ability to file non-executed ISA with FERC after 120 days
77 | Transmission Owner execution |  | 15 business days after Interconnection Customer execution | Status Quo |  | No objection to PJM proposal
78 | Necessary Study Process |  | Separate agreement along with deposit for changes to the ISA after execution at customer request | Status Quo |  | No objection to PJM proposal
79 | Interim rights |  | Captured in Specifications section 2.1 | Status Quo |  | To discuss
80 | Security Requirements |  | 100% for nondirect connection network upgrades First quarter of work for direct connection network upgrades and attachment facilities | 100% of the cost allocation that the customer is responsible for both direct and non-direct connection network upgrades |  | Security posting schedule should be tied to categorization of upgrade (DA vs. shared network upgrades). At-risk amount of security is also based on impact to other same queue interconnection customers
81 | Milestones |  |  |  | If necessary, execution for an Affected System Operating Agreement to fund Affected System Upgrades.
Interconnection Construction Service Agreement
82 | Issuance |  | 45 calendar days after the execution of the ISA | 60 days from the results of the Phase 3 study as a schedule to the ISA |  | Tender draft ISA at the time of the Phase 3 study report
83 | Execution time |  | 90 calendar days from receipt | Same as ISA |  | 90 days for good faith negotiation and execution. Ability to file non-executed ISA with FERC after 120 days
84 | Transmission Owner execution |  | 15 business days after Interconnection Customer execution | Same as ISA |  | No objection to PJM proposal
85 | Option to Build |  | Permitted for Direct Connection Network Upgrades and Transmission Owner Attachment Facilities if elected within 30 calendar days from receipt of Facilities Study | Permitted for Direct Connection Network Upgrades and Transmission Owner Attachment Facilities if elected during Interconnection Customer Decision 1 |  | Permitted for Direct Connection Network Upgrades and Transmission Owner Attachment Facilities if elected 30 CD after Phase 3 report. Transfer of ownership to TP prior to energization
86 | Suspension Provisions |  | 1 year or 3 years if not material to other projects | Not permitted. Issues outside of the customer's control will be dealt with using the ISA/CSA milestones |  | Suspension for 3 years is allowed for DA or non-shared network upgrades. Shared upgrades must be funded during suspension period. Suspension request to be evaluated under an MMA to ensure no impact to other prior or later queued projects. Adjustments to COD should be allowed subject to MMA evaluation but should be limited to a set timeline (x years from queue entrance)
87 | Form of Agreement |  | Separate independent three party agreement | Schedule in the ISA |  | No objection to PJM proposal
Other Independent Items
88 | Overall Timeline |  | 26 months assuming no delays | 24 months |  | 18 months
89 | Application fees supporting the process timeline |  | Fixed based on study phase | See above for study deposits and readiness payments |  | To discuss
90 | TO Procedures for network upgrade and grid enhancing technologies evaluation |  | Transmission Owner specific | Status Quo |  | To discuss
91 | Pre-application process |  | Process to provide limited information prior to entering a formal interconnection request | Remove process | Insitute a process that helps interconnection customer identify the POIs. TOs have the best information about the location, size, etc. of their assets. This information needs to be verified prior to ICs entering the PJM queue. | No objection to PJM proposal
92 | Incremental financial rights |  | Afforded to generation requests building network upgrades that request and meet a certain threshold | Remove ability for generation requests to receive. Previously limited to Transmission Interconnection Customers for AC/DC facilites and Merchant Network upgrades. Since first to cause is no longer a concept, this should be removed |  | No objection to PJM proposal
93 | WMPA treatment |  | State interconnected projects enter the queue with everyone else and sign a WMPA which is not part of the PJM Tariff | Non jurisdictional projects must use the state's process to receive a two party interconnection agreement with the TO/DP prior to entering an interconnection application. WMPA to be incorporated into the PJM Tariff |  | No objection to PJM proposal
92 | Other Request Types |  | All request types currently studied together in the New Services Queue except Attachment RR Generation Interconnection Requests - Attachment N, Y, BB Transmission Interconnection Requests - Attachment S Upgrade Requests - Attachment EE Long Term Firm Transmission Service Requests - Attachment PP Surplus Interconnection Service Requests - Attachment RR | Incorporated in new cycle process: Generation Interconnection Requests Transmission Interconnection Requests Long Term Firm Transmission Service Requests Studied on a parallel process: Upgrade Requests Status Quo: Surplus Interconnection Service Requests
Interim Deliverability
93 | Cost |  | Included in existing study deposits | Status Quo |  | Please provide more details around interim deliverability. Models, study processes etc.
94 | Schedule transparency |  | Results available prior to each auction | Schedule to be posted on website
Reporting Requirements
95 | Reason for delays, suspensions, and timeline |  | PJM required to report to FERC if two consecutive reporting periods exceed the 25% performance threshold outlined in Section 41 of the OATT on a per study phase basis. Suspension timing not publicly available | Status Quo for reporting requirements. Schedule and reasons for any delays will be posted with the updated schedule. All deadlines above using reasonable efforts standard. |  | Queue needs to reflect any approved COD adjustments
96 | Timely communication, transparency, documentation on affected systems, issues and studies |  | Outlined in each regional coordination agreement | Status Quo
Dispute Resolution
97 | Informal Dispute Resolution |  | Per Section 12.1 of OATT | Status Quo
98 | File Unexecuted |  | Interconnection Customer or Transmission Owner may request to have the agreement filed unexecuted with the commission | Status Quo
Transition
99 | Treatment of existing requests |  | N/A | TBD | Preference for AG2 queue projects to be studied under the current PJM interconnection study process with modifications (Draft Transition Proposal No. 2). If AG2 queue projects are to be studied under the new “cluster study” process, this process needs to begin by April 2022. AG2 queue projects should be designated as its own cluster study cycle and not be co-mingled or combined with AH1 or AH2 queue projects in a new cluster study process under any circumstances.
100 | New process implementation date |  | N/A | TBD | TBD (dependent on FERC approval). AG2 Feasibility Studies to be delayed until current PJM Facilities Study backlog is cleared. Work on AH1 & AH2 queue projects to be delayed until AG2 queue projects receive their SIS Report.

## 2a. Design Component Details
Task Force: Interconnection Process Reform
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
Task Force: Interconnection Process Reform
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
Task Force: Interconnection Process Reform
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1
2
3
4
5
6
7
8
9 | [8 empty] | Low
10 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
Task Force: Interconnection Process Reform
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
Task Force: Interconnection Process Reform
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
Task Force: Interconnection Process Reform
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3