## Introduction
Gen Model 2022 Submittal Form (Read Only)
Last Updated: 4/1/2022
Important Considerations to review before using this form: Purpose of this Spreadsheet PJM is issuing this Read-Only Spreadsheet to our members well in advance of the Gen Model MOD-032 Data Submission Window which starts in May. We hope that this spreadsheet will help allow our members to have awareness of the necessary data requirements with sufficient preparation time. This SPREADSHEET IS NOT a replacement for submitting MOD-032 data requirements in the Gen Model Portal. PJM will NOT accept this spreadsheet as evidence of meeting its MOD-032 data requirements. This spreadsheet data must be entered in manually to the Gen Model Website. That is the only official method accepted. PJM is trying to assist our customers by providing a read-only copy of the Portal to assist in data collection. Keep in mind that this Gen Model is a dynamic form and that some of the logic on the Maximum Facility & Seasonal Output Forms (Max Fac & Season Output) were challenging to represent in a static spreadsheet. We did our best to try to make all the questions available. This form is a very close approximation of what is expected for Gen Model 2021 but may not be exactly 100% due to the limitations mentioned earlier. Not all tabs are applicable to all generators. For example, there are tabs applicable to Wind Farms that are not applicable to "Synchronous" Generators as has been in the past with Gen Model. Tabs with the Terms "Sync Gen" relate to the "Synchronous" Generators, "Inv-Based" refer to the "Inverter-Based" Generators, and "Wind Farm" refer to the "Wind Farm" generators. There are several new items that have been added to the Gen Model Form from the 2020 Submittal. Main impacted pages from last year's submittal are the new "Maximum Facility & Seasonal Output", "General Information", "Attachment Line Data", "Step Up Xfmr", "Main Transformers", "Load Transformers" forms. Some of the newer items are still being currently worked on by PJM IT and we are focused on requesting this information in the future. This relates to the capability for users when entering in transformer impedances to be able to automatically convert R + jX based on Load Loss (kW) and %Z of the transformer on its own MVA Base. The ability still exists to enter R + jX just as in previous years but wanted to offer a way to help simplify this task. Only one method is required. There is a possibility that some of the items presented in the Gen Model request may potentially change as IT completes adding these fields to the form. Any changes will be captured in the read-only form and users will be notified as soon as possible. This is not intended or expected but want to bring awareness to this possibility. The "Maximum Facility & Seasonal Output" form is broken out in this read only representation as two different forms. One for Synchronous Generators - "Max Fac & Season Output - Sync", and another form for Wind Farms/Inverter Based Generators - "Max Fac & Season Output - WF-Inv". These forms in particular heavily rely on the updated one-line diagrams which are included in the Gen Model Form and also on the PJM.COM public website. Please make sure you keep these handy as they will help you along your way.
Revision History
| Version # | Date | Notes
| 1 | 2021-04-01 | Final 2021 Gen Model Form Version
| 2 | 2022-04-01 | No changes to Gen model since last window

## General Information
General Information
Individual Completing Data
Plant Information |  |  | Comments
Transmission Owner Area*
Plant Name* |  |  | Select 'Other' as Transmission Owner Area to enter an unlisted plant name
Number of Units* |  |  | Number of machines i.e. a 2x1 combined cycle plant = 3 machines. OR Number of wind/solar aggregated machines to be modeled i.e. 100 MVA wind farm represented by 2 aggregated 50 MVA machines = 2 machines
Name* |  |  | Changing this will not affect PJM account
Email*
Phone Number* |  |  | Changing this will not affect PJM account
Company Name
Plant Location
EIA Plant Code* |  |  | Plant ID from EIA-860 filing
State*
County*
City*
Zip Code*
Single Line Diagram of Plant | Choose File (Provide Attachment)
Generator Details
Commercial Operation Year*

## Sync Gen Parameters
Synchronous Generator
|  |  | Comments | Options
Machine ID* |  |  | All fields should be completed on an individual "Generator Machine ID" basis. Only one value should be entered per Form.
Prime Mover Code* |  |  | From EIA-860 filing | Refer to Item 1 down below.
Energy Source Code* |  |  | From EIA-860 filing | Refer to Item 2 down below.
Terminal Voltage (kV)*
Generator Parameters (All reactances and resistance values in PU on Machine MVA Base at machine terminal voltage)
Combined Turbine-Generator-Exciter Inertia, H [kWs/kVA]
Speed Damping Coefficient, D |  | 0 | 0.5 <= H <= 15
MMWG Procedure Manual and NERC Case Quality Metrics require D=0
Generator Saturation
Generator Saturation at 1.0 p.u. Voltage, S (1.0)
Generator Saturation at 1.2 p.u. Voltage, S (1.2) |  |  | 0 < S1.0
S1.0 <= S1.2
Unsaturated Reactances
Direct Axis Synchronous, Xd(i)
Direct Axis Transient, X'd(i) |  |  | xd < 2.5
Direct Axis Sub-Transient, X"d(i) |  |  | x'd < 0.5 x xd
Quadrature Axis Synchronous, Xq(i) |  |  | x"d <= x'd
Quadrature Axis Transient, X'q(i) |  |  | xq < xd
Quadrature Axis Sub-Transient, X"q(i) * |  |  | x'q < xq
Stator Leakage, Xl |  |  | x"q < x'q
Negative Sequence, X2(i) * |  |  | X"d > XL
Zero Sequence, X0(i) *
Saturated Reactances
Saturated Sub-Transient, X"d(v) *
Transient Reactance, X'd(v)* |  |  | X"d(v) < X"d(i)
Synchronous Reactance, Xd(v)* |  |  | X'd(v) > X"d(v)
Negative Sequence, X2(v)* |  |  | Xd(v) > X'd(v)
Zero Sequence, X0(v) *
Resistances
DC Armature, Ra [Ohms]*
Positive Sequence, R1 *
Negative Sequence, R2 *
Zero Sequence, R0 *
Time Constants
Direct Axis Transient Open Circuit, T'do [sec] |  |  | 1. < T('do < 15.)
Direct Axis Sub-Transient Open Circuit, T"do [sec] |  |  | 0.01 < T"do < 0.2
Quadrature Axis Transient Open Circuit, T'qo [sec] |  |  | T'qo <= T'do
Quadrature Axis Sub-Transient Open Circuit, T"qo [sec] |  |  | T"qo <= T'qo
Armature Three-Phase Short Circuit, Ta3 [sec]*
Stability Models
Generator Models* |  | Choose File (Provide Attachment)
Excitation System Models* |  | Choose File (Provide Attachment)
Governor Models* |  | Choose File (Provide Attachment)
Static Var Compensator (SVC) & Frequency Changer Models |  | Choose File (Provide Attachment)
Power System Stabilizer Models |  | Choose File (Provide Attachment)
Maximum Excitation Limiter Models |  | Choose File (Provide Attachment)
Minimum Excitation Limiter Models |  | Choose File (Provide Attachment)
Compensation Models |  | Choose File (Provide Attachment)
Other documents |  | Choose File (Provide Attachment)
Additional Information for "Options"
Item 1 | Options include ("Steam Turbine (Nuclear, Geo Thermal, Solar (not Combined Cycle)", "Combustion (Gas) Turbine", "Internal Combustion (Diesel, Piston) Engine", "Combined Cycle Steam Part", "Combined Cycle Total Unit (Only for Gens in Planning Stage)", "Combined Cycle Single Shaft (Combustion Turbine and Steam Turbine Share A Single Generator)", "Combined Cycle Combustion Turbine Part (type of coal must be reported as energy source for integrated coal)", "Hydraulic Turbine (includes turbines associated with delivery of water by pipeline)", "Hydraulic Turbine - Reversible (pumped storage), "Photovoltaic", "Wind Turbine", "Compressed Air Energy Storage", "Fuel Cell", "Other", "Unknown at this time (for use for generators in the planning stage)".
Item 2 | Options include ("Agriculture Crop Byproudcts/Straw/Energy Crops", "Anthracite Coal, Bituminous Coal", "Black Liquor", Blast-Furnace Gas", "Coal-based Synfuel and include briquettes, pellets, or extrusions, which are formed by binding materials and processes that recycle material", "Distillate Fuel Oil (includes all Diesel & No. 1, 2, and 4 Fuel Oils)","Geothermal", "Jet Fuel", "Kerosene", Landfill Gas", "Lignite Coal", "Municipal Solid Waste", "Natural Gas", "Nuclear", "Oil-Other and Waste Oil (Butane, Crude Oil, Liquid Byproducts, Oil Waste, Propane, Re-refined Motor Oil, Sludge Oil, Tar Oil)", "Other", "Other (Batteries, Chemicals, Coke Breeze, Hydrogen, Pitch, Sulfur, Tar Coal, & misc. tech)", "Other Biomass Gases (Digester Gas, Methane, & Other)", "Other Biomass Liquids (Ethanol, Fish Oil, Liquid Acetonitrile Waste, Medical Waste, Tall Oil, Waste Alcohol, & Other Liquids not Specified)", "Other Gas (Butane, Coal Processes, Coke-Oven, Refinery, & Other Processes)", "Petroleum Coke", "Propane", "Purchased Steam", "Residual Fuel Oil (includes No. 5 & 6 Fuel Oils & Bunker C Fuel Oil)", "Sludge Waste", "Solar (Photovoltaic, Thermal)", "Subbituminous Coal", "Tires", "Waste/Other Coal (Anthracite Culm, Bituminous Gob, Fine Coal, Lignite Waste, Waste Coal)", "Water (Conventional, Pumped Storage)", "Wind", " Wood Waste Liquids (Red Liquor, Sludge Wood, Spent Sulfite Liquor, and other wood related liquids not specified)", "Wood/Wood Waste Solids (Paper Pellets, Railroad Ties, Utility Poles, Wood Chips, and other wood solids)".

## Sync Gen - Step Up Xfmr
Synchronous Generator - Step Up Transformer
Comments
Select Generator Machine ID(s) for this Transformer
Generator Step-Up (GSU) Transformer Form
Transformer Id* | [7 empty] | List the Transformer ID that the data corresponds with (e.g. EG1, EG2)
Select Transformer Windings* | [7 empty] | Either "Two Windings" or "Three Windings". Each option will have different downstream requirements.
MVA Base* | [7 empty] | Only applicable if "Two Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to low-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base low-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Transformer Ratings
How many ratings does the transformer have?* | [7 empty] | Either "One Rating", "Two Ratings" or "Three Ratings". Each option will have different downstream requirements.
Does the same Rating Set apply for all three windings?* | [7 empty] | When selecting 'Same Rating Set for all three Windings', fill out the Ratings fields as necessary and press the Save button below to automatically populate the remaining grayed fields.
High Winding |  | Low Winding |  |  |  | Tertiary Winding
Rating 1 Cooling Designation* | Rating 1 MVA Rating* | Rating 1 Cooling Designation* |  | Rating 1 MVA Rating* |  | Rating 1 Cooling Designation* | Rating 1 MVA Rating* | Apply as necessary. For example, if "Two Ratings" is selected, only Ratings 1 & 2 will be required.
Rating 2 Cooling Designation* | Rating 2 MVA Rating* | Rating 2 Cooling Designation* |  | Rating 2 MVA Rating* |  | Rating 2 Cooling Designation* | Rating 2 MVA Rating*
Rating 3 Cooling Designation* | Rating 3 MVA Rating* | Rating 3 Cooling Designation* |  | Rating 3 MVA Rating* |  | Rating 3 Cooling Designation* | Rating 3 MVA Rating*
General Transformer Parameters
Core Type* | [7 empty] | Options include ("Single Phase", "Three Phase Shell", "3-Legged, Three Phase", "5-Legged, Three Phase", "7-Legged, Three Phase", "Core, Three Phase Generic", "Other")
K factor (0 <= K <= 2)*
Geomagnetically Induced Current (GIC) Blocking Device* | [7 empty] | Options include ("No", "Yes", "Unknown")
Windings
Photo/Picture of GSU Nameplate, Drawing, and Physical Tap Position information* (E.G., Transformer Factory Test Report) |  |  | Choose File(s) (Provide Attachment)
Is there a Under Load Tap Changer (ULTC)?* |  |  | YES or NO
Location of the ULTC | [7 empty] | Only Applicable if "YES" is selected for "Is there a Under Load Tap Changer (ULTC)?". Options include ("high side", "low side", "tertiary")
If there is no ULTC, is the GSU set to the Neutral Tap? |  |  | YES or NO |  |  |  |  | Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
Where is the tap located that is not set to the Neutral Tap position? | [7 empty] | Even though no ULTC is identified, we are looking for the fixed tap position on the GSU. Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?" AND if "NO" is selected for "If there is no ULTC, is the GSU set to the Neutral Tap?" Options include ("high side", "low side", "tertiary").
Winding Voltages (kV)
High-Side (KV) Nominal (Neutral)* | [7 empty] | Nominal or Neutral Transformer Tap Position
Low-Side (KV) Nominal (Neutral)*
Tertiary (KV) Nominal (Neutral)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "High-Side" is selected for "Location of the ULTC" Question.
Min Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Transformer Step Size (%) for ULTC on high-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "Low-Side" is selected for "Location of the ULTC" Question
Min Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Transformer Step Size (%) for ULTC on low-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Min Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Max Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Transformer Step Size (%) for ULTC on tertiary-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Winding Connection Types (Delta, Wye, Wye Gnd, etc)
High-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Low-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Tertiary* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag"). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Autotransformer* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Any Additional Comments on the Transformer?
Impedances
Provide Impedances Options |  |  | Either (R and X are known) OR (Z (% Impedance & Load Loss (kW) known) |  |  |  |  | Options include ("R and X are known" and "Z (% impedance) and Load Loss (kW) known"). Only one option is required. The items in Beige are required if "Z(% impedance and Load Loss (kW) known") is selected. The items in Purple are required if "R and X are known" is selected.
Z (% Impedance) and Load Loss (kW) Known - Positive Sequence | [7 empty] | Do NOT Select Z(% Impedance & Load Loss (kW) known) option for Transformers that are Single Phase transformers. The calculations are currently arranged only for three phase units.
Z % for the "high-side to low-side" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to low-side" (Three-Windings) or "MVA Base" (Two Windings)
Z % for the "high-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z % for the "low-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base low-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "low-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z (% Impedance) and Load Loss (kW) Known - Zero Sequence
Z % for the "high-side to low-side" transformer winding on its MVA base
Z % for the "high-side to tertiary" transformer winding on its MVA base
Z % for the "low-side to tertiary" transformer winding on its MVA base
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding
Load Loss (kW) for the "low-side to tertiary" transformer winding
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) | [7 empty] | R + jX fields in purple are manually entered fields
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage)
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
DC Winding Resistance
Transformer High Winding DC Resistance (ohms/phase)*
Transformer Low Winding DC Resistance (ohms/phase)
Transformer Tertiary Winding DC Resistance (ohms/phase)
Substation Grounding
Substation grounding DC resistance (ohms)*

## Inv-Based Parameters
Inverter Based - Generator
|  |  | Comments | Options
Inverter Based Parameters
Machine ID*
Prime Mover Code* |  |  |  | Refer to Item 1 down below.
Energy Source Code* |  |  |  | Refer to Item 2 down below.
Type of Inverter Based Technology (e.g. solar, storage, etc.)*
Specify Manufacturer of Inverter*
Specify Model*
MW Value per Inverter (Nominal Rating) (MW)*
Total Number of Inverters*
Terminal Voltage (kV)*
Nominal Output Current at full load per Inverter (Amps)*
Maximum Fault Current Output from the Inverter (Amps or per unit)*
How fast can the Inverter be disconnected from the system subsequent to a fault? (cycles)*
Voltage Relays Installed* |  | YES or NO
Voltage Relay Settings* |  |  | Provide this information if YES to "Voltage Relays Installed" is selected.
Please provide a reactive capability P/Q curve for the inverter * |  | Choose File (Provide Attachment)
Frequency Relays Installed* |  | YES or NO
Frequency Relay Settings* |  |  | Provide this information if YES to "Frequency Relays Installed" is selected.
Please upload the document showing frequency and voltage relay settings for the model* |  | Choose File (Provide Attachment)
Stability Models |  |  | To submit multiple files at once, please place them into a Zip file before uploading.
Generator Models* |  | Choose File (Provide Attachment)
Other Documents |  | Choose File (Provide Attachment)
Additional Information for "Options"
Item 1 | Options include ("Steam Turbine (Nuclear, Geo Thermal, Solar (not Combined Cycle)", "Combustion (Gas) Turbine", "Internal Combustion (Diesel, Piston) Engine", "Combined Cycle Steam Part", "Combined Cycle Total Unit (Only for Gens in Planning Stage)", "Combined Cycle Single Shaft (Combustion Turbine and Steam Turbine Share A Single Generator)", "Combined Cycle Combustion Turbine Part (type of coal must be reported as energy source for integrated coal)", "Hydraulic Turbine (includes turbines associated with delivery of water by pipeline)", "Hydraulic Turbine - Reversible (pumped storage), "Photovoltaic", "Wind Turbine", "Compressed Air Energy Storage", "Fuel Cell", "Other", "Unknown at this time (for use for generators in the planning stage)".
Item 2 | Options include ("Agriculture Crop Byproudcts/Straw/Energy Crops", "Anthracite Coal, Bituminous Coal", "Black Liquor", Blast-Furnace Gas", "Coal-based Synfuel and include briquettes, pellets, or extrusions, which are formed by binding materials and processes that recycle material", "Distillate Fuel Oil (includes all Diesel & No. 1, 2, and 4 Fuel Oils)","Geothermal", "Jet Fuel", "Kerosene", Landfill Gas", "Lignite Coal", "Municipal Solid Waste", "Natural Gas", "Nuclear", "Oil-Other and Waste Oil (Butane, Crude Oil, Liquid Byproducts, Oil Waste, Propane, Re-refined Motor Oil, Sludge Oil, Tar Oil)", "Other", "Other (Batteries, Chemicals, Coke Breeze, Hydrogen, Pitch, Sulfur, Tar Coal, & misc. tech)", "Other Biomass Gases (Digester Gas, Methane, & Other)", "Other Biomass Liquids (Ethanol, Fish Oil, Liquid Acetonitrile Waste, Medical Waste, Tall Oil, Waste Alcohol, & Other Liquids not Specified)", "Other Gas (Butane, Coal Processes, Coke-Oven, Refinery, & Other Processes)", "Petroleum Coke", "Propane", "Purchased Steam", "Residual Fuel Oil (includes No. 5 & 6 Fuel Oils & Bunker C Fuel Oil)", "Sludge Waste", "Solar (Photovoltaic, Thermal)", "Subbituminous Coal", "Tires", "Waste/Other Coal (Anthracite Culm, Bituminous Gob, Fine Coal, Lignite Waste, Waste Coal)", "Water (Conventional, Pumped Storage)", "Wind", " Wood Waste Liquids (Red Liquor, Sludge Wood, Spent Sulfite Liquor, and other wood related liquids not specified)", "Wood/Wood Waste Solids (Paper Pellets, Railroad Ties, Utility Poles, Wood Chips, and other wood solids)".

## Inv-Based - Step Up Xfmr
Inverted Based Generator - Step Up Transformer
Comments
Select Generator Machine ID(s) for this Transformer
Generator Step-Up (GSU) Transformer Form
Transformer Id* | [7 empty] | List the Transformer ID that the data corresponds with (e.g. EG1, EG2)
Select Transformer Windings* | [7 empty] | Either "Two Windings" or "Three Windings". Each option will have different downstream requirements.
MVA Base* | [7 empty] | Only applicable if "Two Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to low-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base low-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Transformer Ratings
How many ratings does the transformer have?* | [7 empty] | Either "One Rating", "Two Ratings" or "Three Ratings". Each option will have different downstream requirements.
Does the same Rating Set apply for all three windings?* | [7 empty] | When selecting 'Same Rating Set for all three Windings', fill out the Ratings fields as necessary and press the Save button below to automatically populate the remaining grayed fields.
High Winding |  | Low Winding |  |  |  | Tertiary Winding
Rating 1 Cooling Designation* | Rating 1 MVA Rating* | Rating 1 Cooling Designation* |  | Rating 1 MVA Rating* |  | Rating 1 Cooling Designation* | Rating 1 MVA Rating*
Rating 2 Cooling Designation* | Rating 2 MVA Rating* | Rating 2 Cooling Designation* |  | Rating 2 MVA Rating* |  | Rating 2 Cooling Designation* | Rating 2 MVA Rating*
Rating 3 Cooling Designation* | Rating 3 MVA Rating* | Rating 3 Cooling Designation* |  | Rating 3 MVA Rating* |  | Rating 3 Cooling Designation* | Rating 3 MVA Rating*
General Transformer Parameters
Core Type* | [7 empty] | Options include ("Single Phase", "Three Phase Shell", "3-Legged, Three Phase", "5-Legged, Three Phase", "7-Legged, Three Phase", "Core, Three Phase Generic", "Other")
K factor (0 <= K <= 2)*
Geomagnetically Induced Current (GIC) Blocking Device* | [7 empty] | Options include ("No", "Yes", "Unknown")
Windings
Photo/Picture of GSU Nameplate, Drawing, and Physical Tap Position information* (E.G., Transformer Factory Test Report) |  |  | Choose File(s) (Provide Attachment)
Is there a Under Load Tap Changer (ULTC)?* |  |  | YES or NO
Location of the ULTC | [7 empty] | Only Applicable if "YES" is selected for "Is there a Under Load Tap Changer (ULTC)?". Options include ("high side", "low side", "tertiary")
If there is no ULTC, is the GSU set to the Neutral Tap? |  |  | YES or NO |  |  |  |  | Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
Where is the tap located that is not set to the Neutral Tap position? | [7 empty] | Even though no ULTC is identified, we are looking for the fixed tap position on the GSU. Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?" AND if "NO" is selected for "If there is no ULTC, is the GSU set to the Neutral Tap?" Options include ("high side", "low side", "tertiary").
Winding Voltages (kV)
High-Side (KV) Nominal (Neutral)* | [7 empty] | Nominal or Neutral Transformer Tap Position
Low-Side (KV) Nominal (Neutral)*
Tertiary (KV) Nominal (Neutral)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Normal (i.e., fixed) Tap Voltage Setting (with respect to ULTC on the high-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "High-Side" is selected for "Location of the ULTC" Question.
Min Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Transformer Step Size (%) for ULTC on high-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "Low-Side" is selected for "Location of the ULTC" Question
Min Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Transformer Step Size (%) for ULTC on low-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Min Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Max Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Transformer Step Size (%) for ULTC on tertiary-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Winding Connection Types (Delta, Wye, Wye Gnd, etc)
High-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Low-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Tertiary* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag"). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Autotransformer* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Any Additional Comments on the Transformer?
Impedances
Provide Impedances Options |  |  | Either (R and X are known) OR (Z (% Impedance & Load Loss (kW) known) |  |  |  |  | Options include ("R and X are known" and "Z (% impedance) and Load Loss (kW) known"). Only one option is required. The items in Beige are required if "Z(% impedance and Load Loss (kW) known") is selected. The items in Purple are required if "R and X are known" is selected.
Z (% Impedance) and Load Loss (kW) Known - Positive Sequence | [7 empty] | Do NOT Select Z(% Impedance & Load Loss (kW) known) option for Transformers that are Single Phase transformers. The calculations are currently arranged only for three phase units.
Z % for the "high-side to low-side" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to low-side" (Three-Windings) or "MVA Base" (Two Windings)
Z % for the "high-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z % for the "low-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base low-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "low-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z (% Impedance) and Load Loss (kW) Known - Zero Sequence
Z % for the "high-side to low-side" transformer winding on its MVA base
Z % for the "high-side to tertiary" transformer winding on its MVA base
Z % for the "low-side to tertiary" transformer winding on its MVA base
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding
Load Loss (kW) for the "low-side to tertiary" transformer winding
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) | [7 empty] | R + jX fields in purple are manually entered fields
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage)
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
DC Winding Resistance
Transformer High Winding DC Resistance (ohms/phase)*
Transformer Low Winding DC Resistance (ohms/phase)
Transformer Tertiary Winding DC Resistance (ohms/phase)
Substation Grounding
Substation grounding DC resistance (ohms)*

## Wind Farm Parameters
Wind Farm Generator - Step Up Transformer
|  |  |  | Comments | Options
Wind Farm Parameters
Machine ID*
Prime Mover Code* |  |  |  |  | Refer to Item 1 down below.
Energy Source Code* |  |  |  |  | Refer to Item 2 down below.
Specify Manufacturer*
Specify Model*
MW Value per Turbine (Nominal Rating) (MW)*
Number of Turbines*
Terminal Voltage (kV)*
Type 4 Turbine*
Stator Resistance, R1 (Ohms)* |  |  |  | Only Appears if "No" is selected for Type 4 Turbine
Saturated Sub-Transient Reactance, X"d(v)* |  |  |  | Only Appears if "No" is selected for Type 4 Turbine
Control Mode* |  |  |  | Options include ("Power Factor", "Voltage Control", "Other")
Voltage Relays Installed* |  | YES or NO
Voltage Relay Settings* |  |  |  | Provide this information if YES to "Voltage Relays Installed" is selected.
Please provide a reactive capability P/Q curve for the inverter * |  | Choose File (Provide Attachment) |  | Provide this information if YES to "Voltage Relays Installed" is selected.
Frequency Relays Installed* |  | YES or NO
Frequency Relay Settings* |  |  |  | Provide this information if YES to "Frequency Relays Installed" is selected.
Please upload the document showing frequency and voltage relay settings for the model* |  | Choose File (Provide Attachment) |  | Provide this information if YES to "Frequency Relays Installed" is selected.
Additional Wind Farm Compensation* |  | YES or NO
Provide Additional Details* |  |  |  | Provide Additional Information if YES to "Additional Wind Farm Compensation is selected.
Stability Models |  |  |  | To submit multiple files at once, please place them into a Zip file before uploading.
Generator Models* |  | Choose File (Provide Attachment)
Upload all applicable files* |  | Choose File (Provide Attachment)
Other Documents |  | Choose File (Provide Attachment)
Additional Information for "Options"
Item 1 | Options include ("Steam Turbine (Nuclear, Geo Thermal, Solar (not Combined Cycle)", "Combustion (Gas) Turbine", "Internal Combustion (Diesel, Piston) Engine", "Combined Cycle Steam Part", "Combined Cycle Total Unit (Only for Gens in Planning Stage)", "Combined Cycle Single Shaft (Combustion Turbine and Steam Turbine Share A Single Generator)", "Combined Cycle Combustion Turbine Part (type of coal must be reported as energy source for integrated coal)", "Hydraulic Turbine (includes turbines associated with delivery of water by pipeline)", "Hydraulic Turbine - Reversible (pumped storage), "Photovoltaic", "Wind Turbine", "Compressed Air Energy Storage", "Fuel Cell", "Other", "Unknown at this time (for use for generators in the planning stage)".
Item 2 | Options include ("Agriculture Crop Byproudcts/Straw/Energy Crops", "Anthracite Coal, Bituminous Coal", "Black Liquor", Blast-Furnace Gas", "Coal-based Synfuel and include briquettes, pellets, or extrusions, which are formed by binding materials and processes that recycle material", "Distillate Fuel Oil (includes all Diesel & No. 1, 2, and 4 Fuel Oils)","Geothermal", "Jet Fuel", "Kerosene", Landfill Gas", "Lignite Coal", "Municipal Solid Waste", "Natural Gas", "Nuclear", "Oil-Other and Waste Oil (Butane, Crude Oil, Liquid Byproducts, Oil Waste, Propane, Re-refined Motor Oil, Sludge Oil, Tar Oil)", "Other", "Other (Batteries, Chemicals, Coke Breeze, Hydrogen, Pitch, Sulfur, Tar Coal, & misc. tech)", "Other Biomass Gases (Digester Gas, Methane, & Other)", "Other Biomass Liquids (Ethanol, Fish Oil, Liquid Acetonitrile Waste, Medical Waste, Tall Oil, Waste Alcohol, & Other Liquids not Specified)", "Other Gas (Butane, Coal Processes, Coke-Oven, Refinery, & Other Processes)", "Petroleum Coke", "Propane", "Purchased Steam", "Residual Fuel Oil (includes No. 5 & 6 Fuel Oils & Bunker C Fuel Oil)", "Sludge Waste", "Solar (Photovoltaic, Thermal)", "Subbituminous Coal", "Tires", "Waste/Other Coal (Anthracite Culm, Bituminous Gob, Fine Coal, Lignite Waste, Waste Coal)", "Water (Conventional, Pumped Storage)", "Wind", " Wood Waste Liquids (Red Liquor, Sludge Wood, Spent Sulfite Liquor, and other wood related liquids not specified)", "Wood/Wood Waste Solids (Paper Pellets, Railroad Ties, Utility Poles, Wood Chips, and other wood solids)".

## Wind Farm - Step Up Xfmr
Wind Farm Generator - Step Up Transformer
Comments
Select Generator Machine ID(s) for this Transformer
Generator Step-Up (GSU) Transformer Form
Transformer Id* | [7 empty] | List the Transformer ID that the data corresponds with (e.g. EG1, EG2)
Select Transformer Windings* | [7 empty] | Either "Two Windings" or "Three Windings". Each option will have different downstream requirements.
MVA Base* | [7 empty] | Only applicable if "Two Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to low-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base low-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Transformer Ratings
How many ratings does the transformer have?* | [7 empty] | Either "One Rating", "Two Ratings" or "Three Ratings". Each option will have different downstream requirements.
Does the same Rating Set apply for all three windings?* | [7 empty] | When selecting 'Same Rating Set for all three Windings', fill out the Ratings fields as necessary and press the Save button below to automatically populate the remaining grayed fields.
High Winding |  | Low Winding |  |  |  | Tertiary Winding
Rating 1 Cooling Designation* | Rating 1 MVA Rating* | Rating 1 Cooling Designation* |  | Rating 1 MVA Rating* |  | Rating 1 Cooling Designation* | Rating 1 MVA Rating*
Rating 2 Cooling Designation* | Rating 2 MVA Rating* | Rating 2 Cooling Designation* |  | Rating 2 MVA Rating* |  | Rating 2 Cooling Designation* | Rating 2 MVA Rating*
Rating 3 Cooling Designation* | Rating 3 MVA Rating* | Rating 3 Cooling Designation* |  | Rating 3 MVA Rating* |  | Rating 3 Cooling Designation* | Rating 3 MVA Rating*
General Transformer Parameters
Core Type* | [7 empty] | Options include ("Single Phase", "Three Phase Shell", "3-Legged, Three Phase", "5-Legged, Three Phase", "7-Legged, Three Phase", "Core, Three Phase Generic", "Other")
K factor (0 <= K <= 2)*
Geomagnetically Induced Current (GIC) Blocking Device* | [7 empty] | Options include ("No", "Yes", "Unknown")
Windings
Photo/Picture of GSU Nameplate, Drawing, and Physical Tap Position information* (E.G., Transformer Factory Test Report) |  |  | Choose File(s) (Provide Attachment)
Is there a Under Load Tap Changer (ULTC)?* |  |  | YES or NO
Location of the ULTC | [7 empty] | Only Applicable if "YES" is selected for "Is there a Under Load Tap Changer (ULTC)?". Options include ("high side", "low side", "tertiary")
If there is no ULTC, is the GSU set to the Neutral Tap? |  |  | YES or NO |  |  |  |  | Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
Where is the tap located that is not set to the Neutral Tap position? | [7 empty] | Even though no ULTC is identified, we are looking for the fixed tap position on the GSU. Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?" AND if "NO" is selected for "If there is no ULTC, is the GSU set to the Neutral Tap?" Options include ("high side", "low side", "tertiary").
Winding Voltages (kV)
High-Side (KV) Nominal (Neutral)* | [7 empty] | Nominal or Neutral Transformer Tap Position
Low-Side (KV) Nominal (Neutral)*
Tertiary (KV) Nominal (Neutral)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Normal (i.e., fixed) Tap Voltage Setting (with respect to ULTC on the high-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "High-Side" is selected for "Location of the ULTC" Question.
Min Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Transformer Step Size (%) for ULTC on high-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "Low-Side" is selected for "Location of the ULTC" Question
Min Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Transformer Step Size (%) for ULTC on low-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Min Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Max Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Transformer Step Size (%) for ULTC on tertiary-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Winding Connection Types (Delta, Wye, Wye Gnd, etc)
High-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Low-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Tertiary* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag"). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Autotransformer* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Any Additional Comments on the Transformer?
Impedances
Provide Impedances Options |  |  | Either (R and X are known) OR (Z (% Impedance & Load Loss (kW) known) |  |  |  |  | Options include ("R and X are known" and "Z (% impedance) and Load Loss (kW) known"). Only one option is required. The items in Beige are required if "Z(% impedance and Load Loss (kW) known") is selected. The items in Purple are required if "R and X are known" is selected.
Z (% Impedance) and Load Loss (kW) Known - Positive Sequence | [7 empty] | Do NOT Select Z(% Impedance & Load Loss (kW) known) option for Transformers that are Single Phase transformers. The calculations are currently arranged only for three phase units.
Z % for the "high-side to low-side" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to low-side" (Three-Windings) or "MVA Base" (Two Windings)
Z % for the "high-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z % for the "low-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base low-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "low-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z (% Impedance) and Load Loss (kW) Known - Zero Sequence
Z % for the "high-side to low-side" transformer winding on its MVA base
Z % for the "high-side to tertiary" transformer winding on its MVA base
Z % for the "low-side to tertiary" transformer winding on its MVA base
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding
Load Loss (kW) for the "low-side to tertiary" transformer winding
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) | [7 empty] | R + jX fields in purple are manually entered fields
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage)
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
DC Winding Resistance
Transformer High Winding DC Resistance (ohms/phase)*
Transformer Low Winding DC Resistance (ohms/phase)
Transformer Tertiary Winding DC Resistance (ohms/phase)
Substation Grounding
Substation grounding DC resistance (ohms)*

## Max Fac & Season Output - Sync
Maximum Facility and Seasonal Output Data (For Synchronous Generators ONLY)
PJM strives to make continuous improvements towards ensuring the fidelity of our modeling data is at a high level. One of the areas of focus for our models is accurately representing the real and reactive capabilities of our generators. The PJM Tariff language with respect to these capabilities can be detailed and intricate. As a result, the amount of specific questions reflect that complexity as shown below.
Comments
Interconnection Agreement Information
Machine Id* |  |  | All fields should be completed on an individual "Generator Machine ID" basis. Only one value should be entered per Form.
Identify Agreement that allows interconnection to PJM* |  |  | Options include ("PJM Interconnection Service Agreement (ISA)", "Interconnection Agreement(s)", "Power Purchase Agreements", "Other")
From Question Above, Provide Additional Information if "Other" is selected. |  |  | If "Other" is selected, provide additional information.
Confirm Interconnection Agreement Documentation *
Queue Number | PJM Queue # |  | Enter PJM Queue #, and/or (Only 1 is required, either Queue Number of the link to the document)
http:// link address | http://link address |  | Enter PJM Interconnection ISA/WMPA link, or FERC filed agreement link.
Interconnection Agreement Documentation | Choose File (Provide Attachment) |  | If no link or Queue # is available, please attach Interconnection agreement file.
If no agreement and/or documentation, provide reasoning. |  |  | If a Queue Number, link to the Interconnection document, or an attachment to the actual agreement is NOT provided, please provide the reasoning why.
Generator D-Curve Information
Is a D-Curve (real vs reactive power output graph) describing the generator’s output capabilities at the normal operating conditions available for upload?”* | Yes or No
Generator D-Curve files* | Choose File (Provide Attachment) |  | If YES is answered above, provide a D-curve for the desired generator. (e.g., provide the closest to operating hydrogen pressure curve if hydrogen cooled)
If No Documentation, Provide Reasoning* |  |  | If NO is answered for the D-curve question for the desired generator, provide additional reasoning.
EIA Information
EIA Plant Code* |  |  | This value should be auto-populated from the field in the General Information.
EIA Generator ID Code(s)* |  |  | There may be situations where the individual generator may be represented by more than one (1) EIA Generator ID.
Generator MVA base (MVA)*
Installed Nameplate Capacity (MW)* |  |  | (Refer to IEEE 762-2006) (Refer to EIA-860 Value)
Nominal Power Factor* |  |  | (Refer to EIA-860 Value)
Maximum Facility Output Information
Provide MW/MVAR per the applicable MFO Conditions
Contractual Maximum Facility Output Information
As-built Generator Maximum Facility Output (MFO) (MW)* |  |  | PJM’s Tariff (http://www.pjm.com/directory/merged-tariffs/oatt.pdf) defines MFO as: Maximum Facility Output: “Maximum Facility Output” shall mean the maximum (not nominal) net electrical power output in megawatts, specified in the Interconnection Service Agreement, after supply of any parasitic or host facility loads, that a Generation Interconnection Customer’s Customer Facility is expected to produce, provided that the specified Maximum Facility Output shall not exceed the output of the proposed Customer Facility that Transmission Provider utilized in the System Impact Study. For plants without an ISA, enter the equivalent value from the applicable Interconnection Agreement. For plants without an Interconnection Agreement, enter the maximum independent net power output. According to the One-Line, (MFO) is also considered as the “Net Plant Output”. If the MFO value written in the agreement at the Plant Level includes more than one generator, only provide the contribution to the MFO from the generator specified at the top of this form.
Is the MFO value in the interconnection service agreement (ISA) based on the output of more than the specified generator?* | Yes or No
What is the MFO value identified in the "Specifications for the ISA"?* |  |  | If YES is selected for the MFO question above, this question will appear. This value will differ from the MFO value above (for the individual generator) because the ISA includes more than the specified generator.
What are the EIA Generator ID(s) of the additional generator(s) associated (including the specified generator) with the interconnection agreement MFO value?* |  |  | If YES is selected for the MFO question above, this question will appear. (e.g., UN1, UN2, UN3, etc.)
How many total generators are included with the MFO in the ISA?* |  |  | If YES is selected for the MFO question above, this question will appear. This number should include the generator of interest. For example, if there are five (5) generators at a EIA Plant including this generator per the ISA agreement, the value would be five (5).
Weather Considerations for MFO
What were the assumptions used to determine the MFO value? * |  |  | Answer all that apply to your generator. If this generator is multi-fueled, assume the fuel that provides the highest plant output.
Ambient Air Temperature (°F) |  |  | If your output is dependent on air temperature, provide assumptions.
Ambient Relative Humidity (%) |  |  | If your output is dependent on humidity, provide assumptions.
Intake Water Temperature (°F) |  |  | If your output is dependent on the intake cooling water, provide assumptions.
Provide Additional information or environmental factors affecting output capability
Reactive Support Device (Item H for Synchronous Generators per the One-Line) (Provide Values at MFO Conditions)
Are there any reactive support devices installed to provide compensation for either/both leading and lagging MVAR capabilities limits per the MFO?* | Yes or No |  | When refering to applicable Reactive Support Devices, it is only referring to network facility upgrade and/or owned facilities.
What is the total MVAR value of the reactive support device(s) used to meet the leading MVAR portion of the PF requirement?* |  |  | If YES is selected for the question Reactive Support question, this question will appear. Only provide the MVAR value of the device that is used to support meeting the Leading PF requirements. It may not be the entire size of the reactive device(s).
What is the total MVAR value of the reactive support device(s) used to meet the lagging MVAR portion of the PF requirement?* |  |  | When refering to applicable Reactive Support Devices, it is only referring to network facility upgrade and/or owned facilities. If YES is selected for the question Reactive Support question, this question will appear. Only provide the MVAR value of the device that is used to support meeting the Lagging PF requirements. It may not be the entire size of the reactive device(s).
Generator Low Side Gross Output (Provide Values at MFO Conditions)
What is the gross output (MW) at the conditions under which MFO is specified?* |  |  | Regarding the Specified Generator Low Side Gross Output (Item A1 for Synchronous Generators) on the One-Line) *
Generator High Side Net Output (Provide Values at MFO Conditions)
What is the High Side Net output (MW) at the conditions under which MFO is specified?* |  |  | Regarding the Specified Generator High Side Net Output (Item E1 for Synchronous only per the One-Line). Losses for some small generators could be negligible. (This is NOT mandatory to provide)
Loads Related to Generation
High Side Connected Transformer Load (Item F for Synchronous Generators on the One-Line) (Provide Values at MFO Conditions)
Is there a High Side Connected Transformer electrically connected to a generator collector bus and support in the output of this individual generator?* | Yes or No |  | High Side Connected Transformer (e.g., station service, "Startup/standby" transformers, etc.) (Refer to Item (F for Synchronous Generators) on the one-line) (Or is netted from the gross output of the unit in Settlements)
What is the real power consumption (MW) of this load?* |  |  | If YES is selected for the question about High Side Connected Transformers, this question will appear. (If more than one of this type of load, provide summation of the loads) (Provide values within 0.1 MW accuracy)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | If YES is selected for the question about High Side Connected Transformers, this question will appear. (If more than one of this type of load, provide summation of the loads) (Provide values within 0.1 MVAR accuracy)
If this load is supporting multiple generators, how much (what %) of the load is consumed by the specified generator?* |  |  | If YES is selected for the question about High Side Connected Transformers, this question will appear. (Select the percentage of load that affects only the specified generator and is applicable to the MFO calculation.)
Remotely Connected Transformer Load (Item G for Synchronous Generators on the One-Line) (Provide Values at MFO Conditions)
Is there a Remotely Connected Transformer electrically connected to the transmission (or distribution) system and support in the output of this individual generator?* | Yes or No |  | Remotely Connected Transformer (e.g., station service, "Startup/standby" transformers, etc.) (Refer to Item G for Synchronous Generators) on the one-line) (Or is netted from the gross output of the unit in PJM Settlements). (Or if this load is wholesale metered).
What is the real power consumption (MW) of this load?* |  |  | If YES is selected for the question about Remotely Connected Transformers, this question will appear. (If more than one of this type of load, provide summation of the loads) (Provide values within 0.1 MW accuracy)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | If YES is selected for the question about Remotely Connected Transformers, this question will appear. (If more than one of this type of load, provide summation of the loads) (Provide values within 0.1 MVAR accuracy)
If this load is supporting multiple generators, how much (what %) of the load is consumed by the specified generator?* |  |  | If YES is selected for the question about Remotely Connected Transformers, this question will appear. (Select the percentage of load that affects only the specified generator and is applicable to the MFO calculation.)
Auxiliary Transformer Load (Item B1 for Synchronous Generators on the One-Line) (Provide Values at MFO Conditions)
Is there an Auxiliary Transformer Load related to the specified generator?* | Yes or No |  | Auxiliary Transformer Load (e.g., Auxiliary Load, Station Service) (Item B1 for Synchronous only per the One-Line)
What is the real power consumption (MW) of this load?* |  |  | If YES is selected for the question about Auxiliary Transformer Loads, this question will appear. (If more than one of this type of load, provide summation of the loads). (Provide values within 0.1 MW accuracy)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | If YES is selected for the question about Auxiliary Transformer Loads, this question will appear. (If more than one of this type of load, provide summation of the loads). (Provide values within 0.1 MVAR accuracy)
Transformer Tertiary Load (Item D1 for Synchronous Generators on the One-Line) (Provide Values at MFO Conditions)
Is there a Transformer Tertiary Load related to the specified generator?* | Yes or No
What is the real power consumption (MW) of this load?* |  |  | If YES is selected for the question about Transformer Tertiary Loads, this question will appear. (If more than one of this type of load, provide summation of the loads). (Provide values within 0.1 MW accuracy).
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | If YES is selected for the question about Transformer Tertiary Loads, this question will appear. (If more than one of this type of load, provide summation of the loads). (Provide values within 0.1 MVAR accuracy)
Power Factor Requirements Section
Power Factor Requirements and Corresponding Questions have multiple different question paths. In order to replicate the dynamic Gen Model Form in a static spreadsheet format, answer the questions in the corresponding questions based on the following color that best represents your generator. This is for Synchronous Generators only.
Has the generator received an ISA or WMPA from PJM?* | YES |  | If your generator meets the Green requirements, answer the questions that are in Green.
Did the generator receive an ISA / WPMA uprate through the PJM Queue?* | YES
Has the generator received an ISA or WMPA from PJM?* | YES |  | If your generator meets the Blue requirements, answer the questions that are in Blue.
Did the generator receive an ISA / WPMA uprate through the PJM Queue?* | NO
Has the generator received an ISA or WMPA from PJM?* | NO |  | If your generator meets the Pink requirements, answer the questions that are in Pink.
If the generator did not enter the PJM Queue, are there any Power Factor (PF) requirements included in the interconnection agreement?* | YES
Has the generator received an ISA or WMPA from PJM?* | NO |  | If your generator meets the Orange requirements, answer the questions that are in Orange.
If the generator did not enter the PJM Queue, are there any Power Factor (PF) requirements included in the interconnection agreement?* | NO
Power Factor Requirements - Queue Information
Has the generator received an ISA or WMPA from PJM?* | YES
Did the generator receive an ISA / WPMA uprate through the PJM Queue?* | YES |  | If YES to the question above (Has the generator received an ISA or WMPA from PJM?), this question will appear.
What is the existing MW portion value per the agreement?* |  |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue) on what is defined as "Existing" portion, or applicable Schedule in the ISA for grandfathered generation).
What is the up-rate MW portion value per the effective agreement?* |  |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue) on what is defined as "Increase" or "Uprate" portion, or applicable Schedule in the ISA for grandfathered generation)
Power Factor Requirements - Existing Portion (Related to the Interconnection Agreement) |  |  | These values should be based on the information found from the Interconnection Agreement (IA)
Where is the PF measurement location of the generator output (related to the existing MW portion)?* |  |  | The options include ("Point of Interconnection - (Item I)" , "Generator Terminals - (Item A1)", "High voltage side of the GSU - (Item E)", "Other Location").
If "Other Location" is selected for the above question, provide additional details. |  |  | Provide details as necessary.
What are the Leading and Lagging Reactive Capability Requirements (related to the existing MW portion)? * Either provide MVARs or PF values. |  |  | PF or MVAR values need to be based on the "existing MW" portion from the Interconnection agreement. However those values need to be based on the gross output of the generator (Item A) per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to the Gross output.
Leading MVAR at Rated Output (Underexcited) |  |  | Either provide MVARs or PF value for Leading reactive capability is required..
Leading PF at Rated Output (Underexcited)
Lagging MVAR at Rated Output (Overexcited) |  |  | Either provide MVARs or PF value for Lagging reactive capability is required..
Lagging PF at Rated Output (Overexcited)
Provide Additional Information for the Leading/Lagging MVAR/PF notes as necessary.
Leading and Lagging MVAR Capabilities - Existing Portion (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions (for the existing MW portion)?*
Leading MVAR at Rated Output (Underexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item A at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Lagging MVAR at Rated Output (Overexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item A at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Power Factor Requirements - Up-rate Portion (Related to the Uprate Interconnection Agreement) |  |  | These values should be based on the information found from the latest (up-rate) Interconnection Agreement (IA)
Where is the PF measurement location of the generator output (related to the up-rate MW portion)?* |  |  | The options include ("Point of Interconnection - (Item I)" , "Generator Terminals) - (Item A1)", "High voltage side of the GSU (Item E)", "Other Location").
If "Other Location" is selected for the above question, provide additional details. |  |  | Provide details as necessary.
What are the Leading and Lagging Reactive Capability Requirements (related to the up-rate MW portion)?* Either provide MVARs or PF values. |  |  | PF or MVAR values need to be based on the "Up-rate MW" portion based on the Interconnection agreement. However those values need to be based on the gross output of the generator (Item A) per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to the Gross output.
Leading MVAR at Rated Output (Underexcited) |  |  | Either provide MVARs or PF value for Leading reactive capability is required..
Leading PF at Rated Output (Underexcited)
Lagging MVAR at Rated Output (Overexcited) |  |  | Either provide MVARs or PF value for Lagging reactive capability is required..
Lagging PF at Rated Output (Overexcited)
Provide Additional Information for the Leading/Lagging MVAR/PF notes as necessary.
Leading and Lagging MVAR Capabilities - Up-rate Portion (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions (for the up-rate MW portion)?*
Leading MVAR at Rated Output (Underexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item A at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross. These MVAR values should INCLUDE both the existing and the up-rate MW portions of the generator. (ENTIRE GEN OUTPUT)
Lagging MVAR at Rated Output (Overexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item A at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross. These MVAR values should INCLUDE both the existing and the up-rate MW portions of the generator. (ENTIRE GEN OUTPUT)
Power Factor Requirements - Queue Information
Has the generator received an ISA or WMPA from PJM?* | YES
Did the generator receive an ISA / WPMA uprate through the PJM Queue?* | NO |  | If YES to the question above (Has the generator received an ISA or WMPA from PJM?), this question will appear.
Power Factor Requirements (Related to the Interconnection Agreement) |  |  | These values should be based on the information found from the Interconnection Agreement (IA).
Where is the PF measurement location of the generator output?* |  |  | The options include ("Point of Interconnection - (Item I)" , "Generator Terminals (Item A1)", "High voltage side of the GSU (Item E)", "Other Location").
If "Other Location" is selected for the above question, provide additional details.
What are the Leading and Lagging Reactive Capability Requirements? * Either provide MVARs or PF values. |  |  | PF or MVAR values need to be based on the Interconnection agreement. However those values need to be based on the gross output of the generator (Item A) per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to the Gross output.
Leading MVAR at Rated Output (Underexcited) |  |  | Either provide MVARs or PF value for Leading reactive capability is required..
Leading PF at Rated Output (Underexcited)
Lagging MVAR at Rated Output (Overexcited) |  |  | Either provide MVARs or PF value for Lagging reactive capability is required..
Lagging PF at Rated Output (Overexcited)
Provide Additional Information for the Leading/Lagging MVAR/PF notes as necessary.
Leading and Lagging MVAR Capabilities (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions?*
Leading MVAR at Rated Output (Underexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item A at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Lagging MVAR at Rated Output (Overexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item A at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Power Factor Requirements - Queue Information
Has the generator received an ISA or WMPA from PJM?* | NO
If the generator did not enter the PJM Queue, are there any Power Factor (PF) requirements included in the interconnection agreement?* | YES |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue), or applicable Schedule in the ISA for grandfathered generation)
Power Factor Requirements (Related to the Interconnection Agreement)
Where is the PF measurement location of the generator output (per interconnection agreement)?* |  |  | The options include ("Point of Interconnection - (Item I)" , "Generator Terminals (Item A1)", "High voltage side of the GSU (Item E)", "Other Location").
What are the Leading and Lagging Requirements portion (per interconnection agreement)?* Either provide MVARs or PF values* |  |  | PF or MVAR values need to be based on the Interconnection agreement. However those values need to be based on the gross output of the generator (Item A) per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to the Gross output.
Leading MVAR at Rated Output (Underexcited) |  |  | Either provide MVARs or PF value for Leading reactive capability is required..
Leading PF at Rated Output (Underexcited)
Lagging MVAR at Rated Output (Overexcited) |  |  | Either provide MVARs or PF value for Lagging reactive capability is required..
Lagging PF at Rated Output (Overexcited)
Provide Additional Information for the Leading/Lagging MVAR/PF notes as necessary.
Leading and Lagging MVAR Capabilities (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions?*
Leading MVAR at Rated Output (Underexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item A at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Lagging MVAR at Rated Output (Overexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item A at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Power Factor Requirements - Queue Information
Has the generator received an ISA or WMPA from PJM?* | NO
If the generator did not enter the PJM Queue, are there any Power Factor (PF) requirements included in the interconnection agreement?* | NO |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue), or applicable Schedule in the ISA for grandfathered generation)
No Interconnection Agreement Power Factor Requirements
If the PF requirement is not documented in the interconnection agreement, please provide reasoning.*
Where is the PF measurement location of the generator output?* |  |  | The options include ("Point of Interconnection - (Item I)" , "Generator Terminals (Item A1)", "High voltage side of the GSU (Item E)", "Other Location").
Leading and Lagging MVAR Capabilities (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions?* |  |  | Back calculate Leading and Lagging MVAR values as if they were measured at Item A1. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Leading MVAR at Rated Output (Underexcited)*
Lagging MVAR at Rated Output (Overexcited)*
Generator Information Related to Process Loads (Only For Synchronous Generators)
Is the individual generator (part of/is) a co-generation plant?* | Yes or No
Is there a Host/Process Load located at this plant related to the specified generator?* | Yes or No |  | Host or Process Load is thermal and/or electrical load consumed by a co-located or nearby facility associated with a co-generator or part of a combined heat and power system. Host/Process Load is essentially a load that is not related to the generating plant "contributing" to its output. Refer to EIA document for more information - https://www.eia.gov/workingpapers/pdf/chp-Industrial_81415.pdf
What type of load is the Process Load?* |  |  | Options include ("Electrical", "Steam", "Other")
If "Other" is Selected, provide additional details.
Where is the Process Load located?* |  |  | Options include ("Low voltage side of the GSU", "Low Voltage Side of the GSU", "Other Location")
If "Other Location" is selected, provide additional details. |  |  | Host/Process Load that is Steam could be located at Point A1 per the one-line but that is technically load before it reaches the generator. In these instances, provide a more detailed explanation by selecting "Other Location".
Is this Process Load included in the MFO value?* | Yes or No
What is the real power consumption (MW) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)
Summer and Winter Peak Output Information
Provide MW/MVAR per the specified Summer and Winter conditions | Refer to the Page 4 of the "Gen Model Diagrams.pdf"
Regarding the Specified Generator Low Side Gross Output (Item A1 on the One-Line): * |  |  | Refer to the Summer and Winter Popups for the seasonal assumptions to use when providing the output values.
| Summer | Winter
Maximum Gross Output (MW) *
Minimum Gross Output (MW) * |  |  | In other words, "What minimum generation level can this generator operate at continuously?"
Installed Capacity (MW) * |  |  | (Refer to IEEE 762-2006) (Refer to EIA-860)
Regarding Specified Generator Net Output (Either at Point E1 or Point I on the One-Line as applicable): *
| Summer | Winter
Maximum Net Output (MW) *
High Side Connected Transformer (Item F on the One-Line)
Is there a High Side Connected Transformer electrically connected to a generator collector bus and support in the output of this individual generator?* | Yes or No |  | High Side Connected Transformer (e.g., station service, "Startup/standby" transformers, etc.)
| Summer | Winter
What is the real power consumption (MW) of this load? * |  |  | (If more than one of this type of load, provide summation of the loads).
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)
If this load is supporting multiple units, how much (what %) of the load is consumed by the specified generator? * |  |  | (Select the percentage of load that affects only the specified generator and is applicable to the MFO calculation.)
Remotely Connected Transformer (Item G on the One-Line)
Is there a Remotely Connected Transformer electrically connected to the transmission (or distribution) system and support in the output of this individual generator?* | Yes or No |  | Remotely Connected Transformer (e.g., station service, "Startup/standby" transformers, etc.)
| Summer | Winter
What is the real power consumption (MW) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)
What is the corresponding reactive power consumption (MVAR) of this load? * |  |  | (If more than one of this type of load, provide summation of the loads)
If this load is supporting multiple units, how much (what %) of the load is consumed by the specified generator? * |  |  | (Select the percentage of load that affects only the specified generator and is applicable to the MFO calculation.)
Auxiliary Transformer Load (Item B1 per the One-Line)
Is there an Auxiliary Transformer Load related to the specified generator?* | Yes or No
| Summer | Winter
What is the real power consumption (MW) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)
Transformer Tertiary Load (Item D1 per the One-Line)
Is there a Transformer Tertiary Load related to the specified generator?* | Yes or No
| Summer | Winter
What is the real power consumption (MW) of this load? * |  |  | (If more than one of this type of load, provide summation of the loads)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)

## Max Fac & Season Output- WF-Inv
Maximum Facility and Seasonal Output Data (For Wind Farm and Inverter Based Generators ONLY)
PJM strives to make continuous improvements towards ensuring the fidelity of our modeling data is at a high level. One of the areas of focus for our models is accurately representing the real and reactive capabilities of our generators. The PJM Tariff language with respect to these capabilities can be detailed and intricate. As a result, the amount of specific questions reflect that complexity as shown below.
Comments
Interconnection Agreement Information
Machine Id* |  |  | All fields should be completed on an individual "Generator Machine ID" basis. Only one value should be entered per Form.
Identify Agreement that allows interconnection to PJM* |  |  | Options include ("PJM Interconnection Service Agreement (ISA)", "Interconnection Agreement(s)", "Power Purchase Agreements", "Other")
From Question Above, Provide Additional Information if "Other" is selected. |  |  | If "Other" is selected, provide additional information.
Confirm Interconnection Agreement Documentation *
Queue Number | PJM Queue # |  | Enter PJM Queue #, and/or (Only 1 is required, either Queue Number of the link to the document)
http:// link address | http://link address |  | Enter PJM Interconnection ISA/WMPA link, or FERC filed agreement link.
Interconnection Agreement Documentation | Choose File (Provide Attachment) |  | If no link or Queue # is available, please attach Interconnection agreement file.
If no agreement and/or documentation, provide reasoning. |  |  | If a Queue Number, link to the Interconnection document, or an attachment to the actual agreement is NOT provided, please provide the reasoning why.
Generator D-Curve Information
Is a D-Curve (real vs reactive power output graph) describing the generator’s output capabilities at the normal operating conditions available for upload?* | Yes or No
Generator D-Curve files* | Choose File (Provide Attachment) |  | If YES is answered above, provide a D-curve for the desired generator. (e.g., provide the closest to operating hydrogen pressure curve if hydrogen cooled)
If No Documentation, Provide Reasoning* |  |  | If NO is answered for the D-curve question for the desired generator, provide additional reasoning.
EIA Information
EIA Plant Code* |  |  | This value should be auto-populated from the field in the General Information.
EIA Generator ID Code(s)* |  |  | There may be situations where the individual generator may be represented by more than one (1) EIA Generator ID.
Generator MVA base (MVA)*
Installed Nameplate Capacity (MW)* |  |  | (Refer to IEEE 762-2006) (Refer to EIA-860 Value)
Nominal Power Factor* |  |  | (Refer to EIA-860 Value)
Maximum Facility Output Information
Provide MW/MVAR per the applicable MFO Conditions
Contractual Maximum Facility Output Information
As-built Generator Maximum Facility Output (MFO) (MW)* |  |  | PJM’s Tariff (http://www.pjm.com/directory/merged-tariffs/oatt.pdf) defines MFO as: Maximum Facility Output: “Maximum Facility Output” shall mean the maximum (not nominal) net electrical power output in megawatts, specified in the Interconnection Service Agreement, after supply of any parasitic or host facility loads, that a Generation Interconnection Customer’s Customer Facility is expected to produce, provided that the specified Maximum Facility Output shall not exceed the output of the proposed Customer Facility that Transmission Provider utilized in the System Impact Study. For plants without an ISA, enter the equivalent value from the applicable Interconnection Agreement. For plants without an Interconnection Agreement, enter the maximum independent net power output. According to the One-Line, (MFO) is also considered as the “Net Plant Output”. If the MFO value written in the agreement at the Plant Level includes more than one generator, only provide the contribution to the MFO from the generator specified at the top of this form.
Is the MFO value in the interconnection service agreement (ISA) based on the output of more than the specified generator?* | Yes or No
What is the MFO value identified in the "Specifications for the ISA"?* |  |  | If YES is selected for the MFO question above, this question will appear. This value will differ from the MFO value above (for the individual generator) because the ISA includes more than the specified generator.
What are the EIA Generator ID(s) of the additional generator(s) associated (including the specified generator) with the interconnection agreement MFO value?* |  |  | If YES is selected for the MFO question above, this question will appear. (e.g., UN1, UN2, UN3, etc.)
How many total generators are included with the MFO in the ISA?* |  |  | If YES is selected for the MFO question above, this question will appear. This number should include the generator of interest. For example, if there are five (5) generators at a EIA Plant including this generator per the ISA agreement, the value would be five (5).
Weather Considerations for MFO
What were the assumptions used to determine the MFO value? * |  |  | Answer all that apply to your generator. If this generator is multi-fueled, assume the fuel that provides the highest plant output.
Ambient Air Temperature (°F) |  |  | If your output is dependent on air temperature, provide assumptions.
Ambient Relative Humidity (%) |  |  | If your output is dependent on humidity, provide assumptions.
Intake Water Temperature (°F) |  |  | If your output is dependent on the intake cooling water, provide assumptions.
Provide additional information or environmental factors affecting output capability
Reactive Support Device (Item N for Wind Farms / Inverter Generators per the One-Line) (Provide Values at MFO Conditions)
Are there any reactive support devices installed to provide compensation for either/both leading and lagging MVAR capabilities limits per the MFO?* | Yes or No
What is the total MVAR value of the reactive support device(s) used to meet the leading MVAR portion of the PF requirement?* |  |  | When refering to applicable Reactive Support Devices, it is only referring to network facility upgrade and/or owned facilities. If YES is selected for the question Reactive Support question, this question will appear. Only provide the MVAR value of the device that is used to support meeting the Leading PF requirements. It may not be the entire size of the reactive device(s).
What is the total MVAR value of the reactive support device(s) used to meet the lagging MVAR portion of the PF requirement?* |  |  | When refering to applicable Reactive Support Devices, it is only referring to network facility upgrade and/or owned facilities. If YES is selected for the question Reactive Support question, this question will appear. Only provide the MVAR value of the device that is used to support meeting the Lagging PF requirements. It may not be the entire size of the reactive device(s).
Generator Low Side Gross Output (Item J1) (Provide Values at MFO Conditions)
What is the Gross Output (MW) at the conditions under which MFO is specified?* |  |  | Regarding the Specified Generator Low Side Gross Output (Item J1 for Wind Farms / Inverter Generators) on the One-Line) *
Loads Related to Generation
Collector Bus Connected Transformer Load (Item L for Wind Farms / Inverter Generators on the One-Line) (Provide Values at MFO Conditions)
Is there a High Side Connected Transformer electrically connected to a generator collector bus and support in the output of this individual generator?* | Yes or No |  | High Side Connected Transformer (e.g., station service, "Startup/standby" transformers, etc.) (Refer to Item L for Wind Farms / Inverter Generators) on the one-line) (Or is netted from the gross output of the unit in Settlements)
What is the real power consumption (MW) of this load? * |  |  | If YES is selected for the question about Collector Bus Connected Transformers, this question will appear. (If more than one of this type of load, provide summation of the loads) (Provide values within 0.1 MW accuracy)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | If YES is selected for the question about Collector Bus Connected Transformers, this question will appear. (If more than one of this type of load, provide summation of the loads) (Provide values within 0.1 MVAR accuracy)
If this load is supporting multiple generators, how much (what %) of the load is consumed by the specified generator?* |  |  | If YES is selected for the question about Collector Bus Connected Transformers, this question will appear. (Select the percentage of load that affects only the specified generator and is applicable to the MFO calculation.)
Remotely Connected Transformer Load (Item M for Wind Farms / Inverter Generators on the One-Line) (Provide Values at MFO Conditions)
Is there a Remotely Connected Transformer electrically connected to the transmission (or distribution) system and support in the output of this individual generator?* | Yes or No |  | Remotely Connected Transformer (e.g., station service, "Startup/standby" transformers, etc.) (Refer to Item (G for Synchronous and M for Wind Farms / Inverter Generators) on the one-line) (Or is netted from the gross output of the unit in PJM Settlements). (Or if this load is wholesale metered).
What is the real power consumption (MW) of this load? * |  |  | If YES is selected for the question about Remotely Connected Transformers, this question will appear. (If more than one of this type of load, provide summation of the loads) (Provide values within 0.1 MW accuracy)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | If YES is selected for the question about Remotely Connected Transformers, this question will appear. (If more than one of this type of load, provide summation of the loads) (Provide values within 0.1 MVAR accuracy)
If this load is supporting multiple generators, how much (what %) of the load is consumed by the specified generator?* |  |  | If YES is selected for the question about Remotely Connected Transformers, this question will appear. (Select the percentage of load that affects only the specified generator and is applicable to the MFO calculation.)
Transformer Tertiary Load (Item P for Wind Farms / Inverter Generators on the One-Line) (Provide Values at MFO Conditions)
Is there a Transformer Tertiary Load related to the specified generator?* | Yes or No
What is the real power consumption (MW) of this load?* |  |  | If YES is selected for the question about Transformer Tertiary Loads, this question will appear. (If more than one of this type of load, provide summation of the loads). (Provide values within 0.1 MW accuracy).
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | If YES is selected for the question about Transformer Tertiary Loads, this question will appear. (If more than one of this type of load, provide summation of the loads). (Provide values within 0.1 MVAR accuracy)
Power Factor Requirements Section
Power Factor Requirements and Corresponding Questions have multiple different question paths. In order to replicate the dynamic Gen Model Form in a static spreadsheet format, answer the questions in the corresponding questions based on the following color that best represents your generator. This is related to the Wind Farm and Inverter Based Generators.
Has the generator received an ISA or WMPA from PJM?* | YES |  | If your generator meets the Green requirements, answer the questions that are in Green.
Did the generator receive an ISA / WPMA uprate through the PJM Queue?* | YES
Has the generator received an ISA or WMPA from PJM?* | YES |  | If your generator meets the Blue requirements, answer the questions that are in Blue.
Did the generator receive an ISA / WPMA uprate through the PJM Queue?* | NO
Has the generator received an ISA or WMPA from PJM?* | NO |  | If your generator meets the Pink requirements, answer the questions that are in Pink.
If the generator did not enter the PJM Queue, are there any Power Factor (PF) requirements included in the interconnection agreement?* | YES
Has the generator received an ISA or WMPA from PJM?* | NO |  | If your generator meets the Orange requirements, answer the questions that are in Orange.
If the generator did not enter the PJM Queue, are there any Power Factor (PF) requirements included in the interconnection agreement?* | NO
Power Factor Requirements - Queue Information
Has the generator received an ISA or WMPA from PJM?* | YES
Did the generator receive an ISA / WPMA uprate through the PJM Queue?* | YES |  | If YES to the question above (Has the generator received an ISA or WMPA from PJM?), this question will appear.
What is the existing MW portion value per the agreement?* |  |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue) on what is defined as "Existing" portion, or applicable Schedule in the ISA for grandfathered generation).
What is the up-rate MW portion value per the effective agreement?* |  |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue) on what is defined as "Increase" or "Uprate" portion, or applicable Schedule in the ISA for grandfathered generation)
PJM Queue Related Information (Related to the Interconnection Agreement) |  |  | These values should be based on the information found from the Interconnection Agreement (IA). Keep in mind that these questions will vary depending on prior answers. This is just a list of potential options. Not all questions will be applicable based on prior selections. Gen Model is a dynamic form and is not easily translatable to a static spreadsheet.
Was the original (i.e., pre-uprate) generator "commercial operation date" (COD) prior to 5/1/2015?* | Yes or No
Was the generator "commercial operation date" (COD) prior to 11/1/2016?* | Yes or No
What was the PJM Queue number for the original generator request?*
Was the queue uprate request for the ISA made prior to 5/1/2015?* | Yes or No
Was the queue uprate request for ISA made prior to 11/1/2016, and the request for the original (i.e., pre-uprate) generator "commercial operation date" (COD) prior to 5/1/2015?* | Yes or No
Was the queue uprate request for the ISA made prior to 11/1/2016?* | Yes or No
Does the ISA identify any Power Factor (PF) requirements?* | Yes or No |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue), or applicable Schedule in the ISA for grandfathered generation)
Does the existing (i.e. no-uprate or pre-uprate MW) portion of the generator MWs include PF requirements?* | Yes or No |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue) on what is defined as "Existing" portion, or applicable Schedule in the ISA for grandfathered generation).
Does the up-rate (i.e., increase MW) portion of the generator include PF requirements?* | Yes or No |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue) on what is defined as "Increase" or "Uprate" portion, or applicable Schedule in the ISA for grandfathered generation)
Power Factor Requirements - Existing Portion (Related to the Interconnection Agreement) |  |  | These values should be based on the information found from the Interconnection Agreement (IA)
Where is the PF measurement location of the generator output (related to the existing MW portion)?* |  |  | The options include ("Point of Interconnection - (Item Q)", "Generator Terminals) - (Item J1)", "High voltage side of the GSU - (Item Q)", "None Required", "Other Location").
If "Other Location" is selected for the above question, provide additional details. |  |  | Provide details as necessary.
What are the Leading and Lagging Reactive Capability Requirements (related to the existing MW portion)? * Either provide MVARs or PF values. |  |  | PF or MVAR values need to be based on the "existing MW" portion from the Interconnection agreement. However those values need to be based on the gross output of the generator (Item J1) per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to the Gross output.
Leading MVAR at Rated Output (Underexcited) |  |  | Either provide MVARs or PF value for Leading reactive capability is required..
Leading PF at Rated Output (Underexcited)
Lagging MVAR at Rated Output (Overexcited) |  |  | Either provide MVARs or PF value for Lagging reactive capability is required..
Lagging PF at Rated Output (Overexcited)
Provide Additional Information for the Leading/Lagging MVAR/PF notes as necessary.
Leading and Lagging MVAR Capabilities - Existing Portion (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions (for the existing MW portion)?*
Leading MVAR at Rated Output (Underexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item J1 at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Lagging MVAR at Rated Output (Overexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item J1 at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Power Factor Requirements - Up-rate Portion (Related to the Uprate Interconnection Agreement) |  |  | These values should be based on the information found from the latest (up-rate) Interconnection Agreement (IA)
Where is the PF measurement location of the generator output (related to the up-rate MW portion)?* |  |  | The options include ("Point of Interconnection - (Item Q)", "Generator Terminals - (Item J1)", "High voltage side of the GSU - (Item Q)", "None Required", "Other Location").
If "Other Location" is selected for the above question, provide additional details. |  |  | Provide details as necessary.
What are the Leading and Lagging Reactive Capability Requirements (related to the up-rate MW portion)?* Either provide MVARs or PF values. |  |  | PF or MVAR values need to be based on the "Up-rate MW" portion based on the Interconnection agreement. However those values need to be based on the gross output of the generator (Item J1) per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to the Gross output.
Leading MVAR at Rated Output (Underexcited) |  |  | Either provide MVARs or PF value for Leading reactive capability is required..
Leading PF at Rated Output (Underexcited)
Lagging MVAR at Rated Output (Overexcited) |  |  | Either provide MVARs or PF value for Lagging reactive capability is required..
Lagging PF at Rated Output (Overexcited)
Provide Additional Information for the Leading/Lagging MVAR/PF notes as necessary.
Leading and Lagging MVAR Capabilities - Up-rate Portion (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions (for the up-rate MW portion)?*
Leading MVAR at Rated Output (Underexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item J1 at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross. These MVAR values should INCLUDE both the existing and the up-rate MW portions of the generator. (ENTIRE GEN OUTPUT)
Lagging MVAR at Rated Output (Overexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item J1 at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross. These MVAR values should INCLUDE both the existing and the up-rate MW portions of the generator. (ENTIRE GEN OUTPUT)
Power Factor Requirements - Queue Information
Has the generator received an ISA or WMPA from PJM?* | YES
Did the generator receive an ISA / WPMA uprate through the PJM Queue?* | NO |  | If YES to the question above (Has the generator received an ISA or WMPA from PJM?), this question will appear.
Power Factor Requirements (Related to the Interconnection Agreement) |  |  | These values should be based on the information found from the Interconnection Agreement (IA).
Where is the PF measurement location of the generator output?* |  |  | The options include ("Point of Interconnection - (Item Q)", "Generator Terminals - (Item J1)", "High voltage side of the GSU - (Item Q)", "None Required", "Other Location").
If "Other Location" is selected for the above question, provide additional details.
What are the Leading and Lagging Reactive Capability Requirements? * Either provide MVARs or PF values. |  |  | PF or MVAR values need to be based on the Interconnection agreement. However those values need to be based on the gross output of the generator (Item J1) per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to the Gross output.
Leading MVAR at Rated Output (Underexcited) |  |  | Either provide MVARs or PF value for Leading reactive capability is required..
Leading PF at Rated Output (Underexcited)
Lagging MVAR at Rated Output (Overexcited) |  |  | Either provide MVARs or PF value for Lagging reactive capability is required..
Lagging PF at Rated Output (Overexcited)
Provide Additional Information for the Leading/Lagging MVAR/PF notes as necessary.
Leading and Lagging MVAR Capabilities (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions?*
Leading MVAR at Rated Output (Underexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item J1 at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Lagging MVAR at Rated Output (Overexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item J1 at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Power Factor Requirements - Queue Information
Has the generator received an ISA or WMPA from PJM?* | NO
If the generator did not enter the PJM Queue, are there any Power Factor (PF) requirements included in the interconnection agreement?* | YES |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue), or applicable Schedule in the ISA for grandfathered generation)
Power Factor Requirements (Related to the Interconnection Agreement)
Where is the PF measurement location of the generator output (per interconnection agreement)?* |  |  | The options include ("Point of Interconnection - (Item Q)", "Generator Terminals - (Item J1)", "High voltage side of the GSU - (Item Q)", "None Required", "Other Location").
What are the Leading and Lagging Requirements portion (per interconnection agreement)?* Either provide MVARs or PF values* |  |  | PF or MVAR values need to be based on the Interconnection agreement. However those values need to be based on the gross output of the generator (Item J1) per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to the Gross output.
Leading MVAR at Rated Output (Underexcited) |  |  | Either provide MVARs or PF value for Leading reactive capability is required..
Leading PF at Rated Output (Underexcited)
Lagging MVAR at Rated Output (Overexcited) |  |  | Either provide MVARs or PF value for Lagging reactive capability is required..
Lagging PF at Rated Output (Overexcited)
Provide Additional Information for the Leading/Lagging MVAR/PF notes as necessary.
Leading and Lagging MVAR Capabilities (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions?*
Leading MVAR at Rated Output (Underexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item J1 at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Lagging MVAR at Rated Output (Overexcited)* |  |  | Actual Leading and Lagging MVAR values as if they were measured at Item J1 at MFO conditions. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Power Factor Requirements - Queue Information
Has the generator received an ISA or WMPA from PJM?* | NO
If the generator did not enter the PJM Queue, are there any Power Factor (PF) requirements included in the interconnection agreement?* | NO |  | (Refer to Section 12 of ISA (ISA established by the PJM Queue), or applicable Schedule in the ISA for grandfathered generation)
No Interconnection Agreement Power Factor Requirements
If the PF requirement is not documented in the interconnection agreement, please provide reasoning.*
Where is the PF measurement location of the generator output?* |  |  | The options include ("Point of Interconnection - (Item Q)", "Generator Terminals - (Item J1)", "High voltage side of the GSU - (Item Q)", "None Required", "Other Location").
Leading and Lagging MVAR Capabilities (Based at MFO Conditions)
What are the Power Factor requirements (i.e., from the D-curve) at the generator terminal for leading and lagging limits at MFO conditions?* |  |  | Back calculate Leading and Lagging MVAR values as if they were measured at Item A1. The MVAR values need to be based on the gross output of the generator per the Machine D-Curve. If the IA describes a net MW output, be sure to adjust the real power output values to Gross.
Leading MVAR at Rated Output (Underexcited)*
Lagging MVAR at Rated Output (Overexcited)*
Summer and Winter Peak Output Information
Provide MW/MVAR per the specified Summer and Winter conditions | Refer to the Page 4 of the "Gen Model Diagrams.pdf"
Regarding the Specified Generator Low Side Gross Output (Item J1 on the One-Line): * |  |  | Refer to the Summer and Winter Popups for the seasonal assumptions to use when providing the output values.
| Summer | Winter
Maximum Gross Output (MW) *
Minimum Gross Output (MW) * |  |  | In other words, "What minimum generation level can this generator operate at continuously?"
Installed Capacity (MW) * |  |  | (Refer to IEEE 762-2006) (Refer to EIA-860)
Regarding Specified Generator Net Power Output (Item Q on the One-Line): *
| Summer | Winter
Maximum Net Output (MW) *
Collector Bus Connected Transformer Load (Item L on the One-Line)
Is there a High Side Connected Transformer electrically connected to a generator collector bus and support in the output of this individual generator?* | Yes or No |  | High Side Connected Transformer (e.g., station service, "Startup/standby" transformers, etc.)
| Summer | Winter
What is the real power consumption (MW) of this load? * |  |  | (If more than one of this type of load, provide summation of the loads).
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)
If this load is supporting multiple units, how much (what %) of the load is consumed by the specified generator? * |  |  | (Select the percentage of load that affects only the specified generator and is applicable to the MFO calculation.)
Remotely Connected Transformer Load (Item M on the One-Line)
Is there a Remotely Connected Transformer electrically connected to the transmission (or distribution) system and support in the output of this individual generator?* | Yes or No |  | Remotely Connected Transformer (e.g., station service, "Startup/standby" transformers, etc.)
| Summer | Winter
What is the real power consumption (MW) of this load? * |  |  | (If more than one of this type of load, provide summation of the loads)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)
If this load is supporting multiple units, how much (what %) of the load is consumed by the specified generator? * |  |  | (Select the percentage of load that affects only the specified generator and is applicable to the MFO calculation.)
Transformer Tertiary Load (Item P per the One-Line)
Is there a Transformer Tertiary Load related to the specified generator?* | Yes or No
| Summer | Winter
What is the real power consumption (MW) of this load? * |  |  | (If more than one of this type of load, provide summation of the loads)
What is the corresponding reactive power consumption (MVAR) of this load?* |  |  | (If more than one of this type of load, provide summation of the loads)

## CB and Relays
Circuit Breakers and Relays
Submit data for Circuit Breakers and Relays |  | Comments
Circuit Breaker and Relay Parameters
Substation Name*
Breaker Name*
Manufacturer*
Model Number*
Nameplate Interrupting Rating (kA or MVA)*
Nameplate Rating Type* |  | Options include ("kA" or "MVA")
Nameplate Interrupting Time (cycles)*
Nameplate K-factor
Nameplate Max Design (kV)*
Operating kV*
Contact Parting Time (cycles)*
Protective Equipment 1 (i.e.,generator, line, transformer)*
Protective Equipment 2 (i.e.,generator, line, transformer)*
Interrupting Medium (i.e., Gas, Oil, Air, Etc)
Reclosing Time One (seconds)
Reclosing Time Two (seconds)
Is Underfrequency (UF) protection installed?* | YES or NO
Instantaneous UF Setting (Hz) |  | If YES is selected for "Is Underfrequency (UF) protection installed?, provide information in this field.
Short-Term Delayed UF Setting (Hz) |  | If YES is selected for "Is Underfrequency (UF) protection installed?, provide information in this field.
Short-Term Delayed UF Setting (Cycles) |  | If YES is selected for "Is Underfrequency (UF) protection installed?, provide information in this field.
Longer-Term Delayed UF Setting (Hz) |  | If YES is selected for "Is Underfrequency (UF) protection installed?, provide information in this field.
Longer-Term Delayed UF Setting (Cycles) |  | If YES is selected for "Is Underfrequency (UF) protection installed?, provide information in this field.
Is Overfrequency (OF) protection installed?* | YES or NO
Instantaneous OF Setting (Hz) |  | If YES is selected for "Is Overfrequency (OF) protection installed?, provide information in this field.
Short-Term Delayed OF Setting (Hz) |  | If YES is selected for "Is Overfrequency (OF) protection installed?, provide information in this field.
Short-Term Delayed OF Setting (Cycles) |  | If YES is selected for "Is Overfrequency (OF) protection installed?, provide information in this field.
Longer-Term Delayed OF Setting (Hz) |  | If YES is selected for "Is Overfrequency (OF) protection installed?, provide information in this field.
Longer-Term Delayed OF Setting (Cycles) |  | If YES is selected for "Is Overfrequency (OF) protection installed?, provide information in this field.
Is Undervoltage (UV) protection installed?* | YES or NO
Nominal Voltage Level (kV) |  | If YES is selected for "Is Undervoltage (UV) protection installed?, provide information in this field. Provide the “Nominal Voltage Level” ONLY if the point of measurement of the relay is NOT the generator terminal voltage (e.g., Point Of Interconnection Voltage). If the relay is associated with its terminal voltage, leave this field blank.
Instantaneous UV Setting (pu of Nominal Voltage) |  | If YES is selected for "Is Undervoltage (UV) protection installed?, provide information in this field.
Short-Term Delayed UV Setting (pu of Nominal Voltage) |  | If YES is selected for "Is Undervoltage (UV) protection installed?, provide information in this field.
Short-Term Delayed UV Setting (cycles) |  | If YES is selected for "Is Undervoltage (UV) protection installed?, provide information in this field.
Longer-Term Delayed UV Setting (pu of Nominal Voltage) |  | If YES is selected for "Is Undervoltage (UV) protection installed?, provide information in this field.
Longer-Term Delayed UV Setting (Cycles) |  | If YES is selected for "Is Undervoltage (UV) protection installed?, provide information in this field.
Is Overvoltage (OV) protection installed?* | YES or NO
Nominal Voltage Level (kV) |  | If YES is selected for "Is Overvoltage (OV) protection installed?, provide information in this field. Provide the “Nominal Voltage Level” ONLY if the point of measurement of the relay is NOT the generator terminal voltage (e.g., Point Of Interconnection Voltage). If the relay is associated with its terminal voltage, leave this field blank.
Instantaneous OV Setting (pu of Nominal Voltage) |  | If YES is selected for "Is Overvoltage (OV) protection installed?, provide information in this field.
Short-Term Delayed OV Setting (pu of Nominal Voltage) |  | If YES is selected for "Is Overvoltage (OV) protection installed?, provide information in this field.
Short-Term Delayed OV Setting (cycles) |  | If YES is selected for "Is Overvoltage (OV) protection installed?, provide information in this field.
Longer-Term Delayed OV Setting (pu of Nominal Voltage) |  | If YES is selected for "Is Overvoltage (OV) protection installed?, provide information in this field.
Longer-Term Delayed OV Setting (Cycles) |  | If YES is selected for "Is Overvoltage (OV) protection installed?, provide information in this field.

## Main Transformers
Main Transformer
Comments
Select Generator Machine ID(s) for this Transformer
Transformer Form
Transformer Id* | [7 empty] | List the Transformer ID that the data corresponds with (e.g. EG1, EG2)
Select Transformer Windings* | [7 empty] | Either "Two Windings" or "Three Windings". Each option will have different downstream requirements.
MVA Base* | [7 empty] | Only applicable if "Two Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to low-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base low-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Transformer Ratings
How many ratings does the transformer have?* | [7 empty] | Either "One Rating", "Two Ratings" or "Three Ratings". Each option will have different downstream requirements.
Does the same Rating Set apply for all three windings?* | [7 empty] | When selecting 'Same Rating Set for all three Windings', fill out the Ratings fields as necessary and press the Save button below to automatically populate the remaining grayed fields.
High Winding |  | Low Winding |  |  |  | Tertiary Winding
Rating 1 Cooling Designation* | Rating 1 MVA Rating* | Rating 1 Cooling Designation* |  | Rating 1 MVA Rating* |  | Rating 1 Cooling Designation* | Rating 1 MVA Rating*
Rating 2 Cooling Designation* | Rating 2 MVA Rating* | Rating 2 Cooling Designation* |  | Rating 2 MVA Rating* |  | Rating 2 Cooling Designation* | Rating 2 MVA Rating*
Rating 3 Cooling Designation* | Rating 3 MVA Rating* | Rating 3 Cooling Designation* |  | Rating 3 MVA Rating* |  | Rating 3 Cooling Designation* | Rating 3 MVA Rating*
General Transformer Parameters
Core Type* | [7 empty] | Options include ("Single Phase", "Three Phase Shell", "3-Legged, Three Phase", "5-Legged, Three Phase", "7-Legged, Three Phase", "Core, Three Phase Generic", "Other")
K factor (0 <= K <= 2)*
Geomagnetically Induced Current (GIC) Blocking Device* | [7 empty] | Options include ("No", "Yes", "Unknown")
Windings
Photo/Picture of GSU Nameplate, Drawing, and Physical Tap Position information* (E.G., Transformer Factory Test Report) |  |  | Choose File(s) (Provide Attachment)
Is there a Under Load Tap Changer (ULTC)?* |  |  | YES or NO
Location of the ULTC | [7 empty] | Only Applicable if "YES" is selected for "Is there a Under Load Tap Changer (ULTC)?". Options include ("high side", "low side", "tertiary")
If there is no ULTC, is the GSU set to the Neutral Tap? |  |  | YES or NO |  |  |  |  | Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
Where is the tap located that is not set to the Neutral Tap position? | [7 empty] | Even though no ULTC is identified, we are looking for the fixed tap position on the GSU. Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?" AND if "NO" is selected for "If there is no ULTC, is the GSU set to the Neutral Tap?" Options include ("high side", "low side", "tertiary").
Winding Voltages (kV)
High-Side (KV) Nominal (Neutral)* | [7 empty] | Nominal or Neutral Transformer Tap Position
Low-Side (KV) Nominal (Neutral)*
Tertiary (KV) Nominal (Neutral)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Normal (i.e., fixed) Tap Voltage Setting (with respect to ULTC on the high-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "High-Side" is selected for "Location of the ULTC" Question.
Min Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Transformer Step Size (%) for ULTC on high-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "Low-Side" is selected for "Location of the ULTC" Question
Min Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Transformer Step Size (%) for ULTC on low-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Min Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Max Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Transformer Step Size (%) for ULTC on tertiary-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Winding Connection Types (Delta, Wye, Wye Gnd, etc)
High-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Low-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Tertiary* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag"). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Autotransformer* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Any Additional Comments on the Transformer?
Impedances
Provide Impedances Options |  |  | Either (R and X are known) OR (Z (% Impedance & Load Loss (kW) known) |  |  |  |  | Options include ("R and X are known" and "Z (% impedance) and Load Loss (kW) known"). Only one option is required. The items in Beige are required if "Z(% impedance and Load Loss (kW) known") is selected. The items in Purple are required if "R and X are known" is selected.
Z (% Impedance) and Load Loss (kW) Known - Positive Sequence | [7 empty] | Do NOT Select Z(% Impedance & Load Loss (kW) known) option for Transformers that are Single Phase transformers. The calculations are currently arranged only for three phase units.
Z % for the "high-side to low-side" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to low-side" (Three-Windings) or "MVA Base" (Two Windings)
Z % for the "high-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z % for the "low-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base low-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "low-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z (% Impedance) and Load Loss (kW) Known - Zero Sequence
Z % for the "high-side to low-side" transformer winding on its MVA base
Z % for the "high-side to tertiary" transformer winding on its MVA base
Z % for the "low-side to tertiary" transformer winding on its MVA base
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding
Load Loss (kW) for the "low-side to tertiary" transformer winding
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) | [7 empty] | R + jX fields in purple are manually entered fields
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage)
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
DC Winding Resistance
Transformer High Winding DC Resistance (ohms/phase)*
Transformer Low Winding DC Resistance (ohms/phase)
Transformer Tertiary Winding DC Resistance (ohms/phase)
Substation Grounding
Substation grounding DC resistance (ohms)*

## Load Transformers
Load Transformer
Comments
Select data for Load Transformer
Transformer Form
Transformer Id* | [7 empty] | List the Transformer ID that the data corresponds with (e.g. EG1, EG2)
Select Transformer Windings* | [7 empty] | Either "Two Windings" or "Three Windings". Each option will have different downstream requirements.
MVA Base* | [7 empty] | Only applicable if "Two Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to low-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base high-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
MVA Base low-side to tertiary | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Transformer Ratings
How many ratings does the transformer have?* | [7 empty] | Either "One Rating", "Two Ratings" or "Three Ratings". Each option will have different downstream requirements.
Does the same Rating Set apply for all three windings?* | [7 empty] | When selecting 'Same Rating Set for all three Windings', fill out the Ratings fields as necessary and press the Save button below to automatically populate the remaining grayed fields.
High Winding |  | Low Winding |  |  |  | Tertiary Winding
Rating 1 Cooling Designation* | Rating 1 MVA Rating* | Rating 1 Cooling Designation* |  | Rating 1 MVA Rating* |  | Rating 1 Cooling Designation* | Rating 1 MVA Rating*
Rating 2 Cooling Designation* | Rating 2 MVA Rating* | Rating 2 Cooling Designation* |  | Rating 2 MVA Rating* |  | Rating 2 Cooling Designation* | Rating 2 MVA Rating*
Rating 3 Cooling Designation* | Rating 3 MVA Rating* | Rating 3 Cooling Designation* |  | Rating 3 MVA Rating* |  | Rating 3 Cooling Designation* | Rating 3 MVA Rating*
General Transformer Parameters
Core Type* | [7 empty] | Options include ("Single Phase", "Three Phase Shell", "3-Legged, Three Phase", "5-Legged, Three Phase", "7-Legged, Three Phase", "Core, Three Phase Generic", "Other")
K factor (0 <= K <= 2)*
Geomagnetically Induced Current (GIC) Blocking Device* | [7 empty] | Options include ("No", "Yes", "Unknown")
Windings
Photo/Picture of GSU Nameplate, Drawing, and Physical Tap Position information* (E.G., Transformer Factory Test Report) |  |  | Choose File(s) (Provide Attachment)
Is there a Under Load Tap Changer (ULTC)?* |  |  | YES or NO
Location of the ULTC | [7 empty] | Only Applicable if "YES" is selected for "Is there a Under Load Tap Changer (ULTC)?". Options include ("high side", "low side", "tertiary")
If there is no ULTC, is the GSU set to the Neutral Tap? |  |  | YES or NO |  |  |  |  | Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
Where is the tap located that is not set to the Neutral Tap position? | [7 empty] | Even though no ULTC is identified, we are looking for the fixed tap position on the GSU. Only applicable if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?" AND if "NO" is selected for "If there is no ULTC, is the GSU set to the Neutral Tap?" Options include ("high side", "low side", "tertiary").
Winding Voltages (kV)
High-Side (KV) Nominal (Neutral)* | [7 empty] | Nominal or Neutral Transformer Tap Position
Low-Side (KV) Nominal (Neutral)*
Tertiary (KV) Nominal (Neutral)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Normal (i.e., fixed) Tap Voltage Setting (with respect to ULTC on the high-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "High-Side" is selected for "Location of the ULTC" Question.
Min Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the high-side) (kV)*
Transformer Step Size (%) for ULTC on high-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)* | [7 empty] | Normal (Fixed) Tap Setting refers to the Tap that the GSU is currently set at. Only applicable if "Low-Side" is selected for "Location of the ULTC" Question
Min Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Max Tap Voltage Setting (with respect to the ULTC on the low-side) (kV)*
Transformer Step Size (%) for ULTC on low-side*
Normal (i.e., fixed) Tap Voltage Setting (with respect to the ULTC on tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Min Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Max Tap Voltage Setting (with respect to the ULTC on the tertiary-side) (kV)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Transformer Step Size (%) for ULTC on tertiary-side* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question.
Winding Connection Types (Delta, Wye, Wye Gnd, etc)
High-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Low-Side* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Tertiary* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag"). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Autotransformer* | [7 empty] | Options for all types include ("Delta", "Wye", "Auto Wye", "Grounded Wye", "Zigzag").
Any Additional Comments on the Transformer?
Impedances
Provide Impedances Options |  |  | Either (R and X are known) OR (Z (% Impedance & Load Loss (kW) known) |  |  |  |  | Options include ("R and X are known" and "Z (% impedance) and Load Loss (kW) known"). Only one option is required. The items in Beige are required if "Z(% impedance and Load Loss (kW) known") is selected. The items in Purple are required if "R and X are known" is selected.
Z (% Impedance) and Load Loss (kW) Known - Positive Sequence | [7 empty] | Do NOT Select Z(% Impedance & Load Loss (kW) known) option for Transformers that are Single Phase transformers. The calculations are currently arranged only for three phase units.
Z % for the "high-side to low-side" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to low-side" (Three-Windings) or "MVA Base" (Two Windings)
Z % for the "high-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base high-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z % for the "low-side to tertiary" transformer winding on its MVA base | [7 empty] | MVA Base is based on the "MVA Base low-side to tertiary" (Three-Windings). Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Load Loss (kW) for the "low-side to tertiary" transformer winding | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Z (% Impedance) and Load Loss (kW) Known - Zero Sequence
Z % for the "high-side to low-side" transformer winding on its MVA base
Z % for the "high-side to tertiary" transformer winding on its MVA base
Z % for the "low-side to tertiary" transformer winding on its MVA base
Load Loss (kW) for the "high-side to low-side" transformer winding
Load Loss (kW) for the "high-side to tertiary" transformer winding
Load Loss (kW) for the "low-side to tertiary" transformer winding
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) from %Z and Load Loss | [7 empty] | Only applicable if "Z (% impedance) and Load Loss (kW) known".
|  |  | R |  | X
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Positive Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage) | [7 empty] | R + jX fields in purple are manually entered fields
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Zero Sequence Impedances (All values in PU on Transformer MVA Base at nominal winding voltage)
|  |  | R |  | X |  |  | Only applicable if "R and X are known" or if "NO" is selected for "Is there a Under Load Tap Changer (ULTC)?"
High-Side to Low-Side (PU)*
High-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
Low-Side to Tertiary (PU)* | [7 empty] | Only applicable if "Three Windings" Selected for "Select Transformer Windings" Question
DC Winding Resistance
Transformer High Winding DC Resistance (ohms/phase)*
Transformer Low Winding DC Resistance (ohms/phase)
Transformer Tertiary Winding DC Resistance (ohms/phase)
Substation Grounding
Substation grounding DC resistance (ohms)*

## Attachment Line Data
Attachment Line Data
Select data for Attachment Line(s)
Attachment Line Form |  |  | Comments | Options
Select Generator Machine ID(s) for this Attachment line* |  |  | Select Generator associated with associated Attachment line.
Attachment Line ID* |  |  | Provide a name for each individual attachment line. All fields should be completed on an individual "Attachment Lines" basis. Only one value should be entered per Form.
Voltage level* (kV)
MVA base* |  | 100 | 100 MVA Base is fixed for all attachment lines.
Is line length greater than 0.2 miles? |  | YES or NO | All ratings information is STILL required for ALL lines for FAC-008 data requirements. If line is less than 0.2 miles, "Impedance" information is not required.
Attachment line length* (miles) |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears.
Conductor type |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears. | Refer to Item 1 down below.
Conductor type (Other) |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears. If "Other" is selected, provide the information.
Impedances on 100 MVA Base (R + jX; B)
Total branch positive sequence impedance |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears. Provide the value in pu (Per Unit on 100 MVA base).
R (pu) |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears. Provide the value in pu (Per Unit on 100 MVA base).
X (pu) |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears. Provide the value in pu (Per Unit on 100 MVA base).
Total branch zero sequence impedance
R (pu) |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears. Provide the value in pu (Per Unit on 100 MVA base).
X (pu) |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears. Provide the value in pu (Per Unit on 100 MVA base).
Total branch charging (B) susceptance
B (pu) |  |  | If YES is selected for "Is line length greater than 0.2 miles?", this question appears. Provide the value in pu (Per Unit on 100 MVA base).
Ratings
Normal* (MVA) |  |  | Refer to FAC-008 facility ratings guidance. Provide at least one rating.
Short-Term Emergency (MVA) |  |  | Refer to FAC-008 facility ratings guidance. Provide at least one rating.
Long-Term Emergency (MVA) |  |  | Refer to FAC-008 facility ratings guidance. Provide at least one rating.
Comments |  |  | Provide any comments regarding the attachment line configurations such as if there's 1 attachment line, 2 parallel attachment lines with the same impedance as input above, etc.
Additional Information for "Options"
Item 1 | Options include ("AAAC", "AAC", "ACAR", "ACCC", "ACCR", "ACSSTW", "ACSR", "AACSR", "AACTW", "ACSS", "ACRTW", "Other").

## Additional Data Files
Attachment Files
The current file size limit per entry is 25MB.
Gen Model allows users to upload the files with following extensions. Please make sure to provide any attachment in the approved file types.
.dll | .out
.obj | .log
.lib | .dyr
.for | .snp
.f | .sav
.f90 | .raw
.txt | .cnv
.idv | .sld
.py | .sbs
.rsp | .irf
.flx | .psa
.dat | .pdf
.bin | .jpeg
.bat | .jpg
.tif | .xls
.dgn | .xlsx
.dxf | .doc
.dwg | .docx
.rar | .zip