## 2020-2021 Parameters
2020-2021 RPM Base Residual Auction Planning Parameters |  |  |  | #47825914 |  | 2017-05-23
| RTO | Notes:
Installed Reserve Margin (IRM) | 16.6% | 2016 IRM Study
Pool-Wide Average EFORd | 6.59% | 2016 IRM Study
Forecast Pool Requirement (FPR) | 1.0892 | 2016 IRM Study
Preliminary Forecast Peak Load | 153915 | Load data: from 2017 Load Report with adjustments due to load served outside PJM.
Locational Deliverability Area
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL | DAYTON | DEOK
CETO | NA | -7000 | 3650 | 2900 | 5900 | 2620 | 1230 | 1540 | 4660 | 3540 | 640 | 4410 | -1010 | 2550 | 3650
CETL | NA | 4218 | 8800 | 9802 | 8001 | 4264 | 1872 | 7625 | 9889 | 5605 | 4064 | 6244 | 7084 | 3401 | 5072
Reliability Requirement | 167644.2 | 66385 | 36921 | 15486 | 11797 | 6023 | 2999 | 7978 | 15610 | 5865 | 26224 | 8132 | 9829 | 4027 | 7500
Total Peak Load of FRR Entities | 12200.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 875.5
Preliminary FRR Obligation | 13288.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 953.6
Reliability Requirement adjusted for FRR | 154355.3 | 66385 | 36921 | 15486 | 11797 | 6023 | 2999 | 7978 | 15610 | 5865 | 26224 | 8132 | 9829 | 4027 | 7102.3488
Gross CONE, $/MW-Day (UCAP Price) | 394.43 | 394.55 | 393.93 | 401.04 | 393.93 | 393.93 | 393.93 | 401.04 | 391.3 | 391.3 | 391.3 | 401.04 | 391.45 | 391.3 | 391.3
Net CONE, $/MW-Day (UCAP Price) | 292.95 | 252.4 | 283.1 | 202.43 | 306.92 | 306.92 | 254.97 | 226.53 | 261.17 | 261.17 | 329.81 | 178.33 | 267.33 | 273.14 | 282.46
EE Addback (UCAP) | 2432.8 | 775.3 | 416.9 | 273 | 127.9 | 25.5 | 11 | 95 | 47.2 | 0.6 | 830.3 | 178 | 49.1 | 47.1 | 84.4
Variable Resource Requirement Curve:
Point (a) UCAP Price, $/MW-Day | 439.43 | 394.55 | 424.65 | 401.04 | 460.38 | 460.38 | 393.93 | 401.04 | 391.76 | 391.76 | 494.72 | 401.04 | 401 | 409.71 | 423.69
Point (b) UCAP Price, $/MW-Day | 219.71 | 189.3 | 212.33 | 151.82 | 230.19 | 230.19 | 191.23 | 169.9 | 195.88 | 195.88 | 247.36 | 133.75 | 200.5 | 204.86 | 211.85
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Point (a) UCAP Level, MW | 156523.3 | 67046.4 | 37274.6 | 15732.4 | 11904.7 | 6038.2 | 3004.9 | 8059.3 | 15630.4 | 5855.5 | 27009.3 | 8296.1 | 9861.2 | 4067.2 | 7174.6
Point (b) UCAP Level, MW | 160627.1 | 68811.4 | 38256.2 | 16144.2 | 12218.3 | 6198.3 | 3084.6 | 8271.4 | 16045.4 | 6011.5 | 27706.5 | 8512.3 | 10122.6 | 4174.3 | 7363.4
Point (c) UCAP Level, MW | 168437.6 | 72170.5 | 40124.4 | 16927.8 | 12815.2 | 6503.1 | 3236.3 | 8675.1 | 16835.3 | 6308.2 | 29033.5 | 8923.7 | 10619.9 | 4378 | 7722.8
Nominated PRD Value, MW | 558 | 558 | 58 | 500 | 0 | 0 | 27 | 170 | 0 | 0 | 0 | 330 | 0 | 0 | 0
VRR Curve adjusted for PRD:
Point (a1) UCAP Price, $/MW-Day | 439.43 | 394.55 | 424.65 | 401.04 |  |  | 393.93 | 401.04 |  |  |  | 401.04
Point (b1) UCAP Price, $/MW-Day | 219.71 | 189.3 | 212.33 | 151.82 |  |  | 191.23 | 169.9 |  |  |  | 133.75
Point (prd1) UCAP Price, $/MW-Day | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01 |  |  |  | 0.01
Point (prd2) UCAP Price, $/MW-Day | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01 |  |  |  | 0.01
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  | 0
Point (a1) UCAP Level, MW | 155915.5 | 66438.6 | 37211.4 | 15187.8 |  |  | 2975.5 | 7874.1 |  |  |  | 7936.7
Point (b1) UCAP Level, MW | 160019.3 | 68203.6 | 38193 | 15599.6 |  |  | 3055.2 | 8086.2 |  |  |  | 8152.9
Point (prd1) UCAP Level, MW | 167829.4 | 71562.5 | 40061.1 | 16383.1 |  |  | 3206.9 | 8489.9 |  |  |  | 8564.3
Point (prd2) UCAP Level, MW | 168437.2 | 72170.3 | 40124.3 | 16927.7 |  |  | 3236.3 | 8675.1 |  |  |  | 8923.7
Point (c) UCAP Level, MW | 168437.6 | 72170.5 | 40124.4 | 16927.8 |  |  | 3236.3 | 8675.1 |  |  |  | 8923.7
Pre-Auction Credit Rate, $/MW | 53463.38 | 46063 | 51665.75 | 36943.48 | 56012.9 | 56012.9 | 46532.03 | 41341.73 | 47663.53 | 47663.53 | 60190.33 | 32545.23 | 48787.73 | 49848.05 | 51548.95
Post-Auction Credit Rate, $/MW | 53463.375 | 46063 | 51665.75 | 36943.475 | 56012.9 | 56012.9 | 46532.025 | 41341.725 | 47663.525 | 47663.525 | 60190.325 | 32545.225 | 48787.725 | 49848.05 | 51548.95
Participant-Funded ICTRs Awarded | NA | 1557 | 40 | NA | 41 | 21 | 72 | NA | NA | NA | NA | 65.7 | NA | NA | 155
FRR Load Requirement (% Obligation):
Minimum Internal Resource Requirement | NA | 100% | 85% | 40.6% | 36.1% | NA | NA | NA | NA | NA | 94.2% | 26.4% | NA | NA | 41.7%
LDA CETO/CETL Data; Zonal Peak Loads, Base Zonal FRR Scaling Factors, and FRR load.
LDA/Zone | CETO | CETL | CETL to CETO Ratio % | 2016 Zonal W/N Coincident Peak Loads | Preliminary Zonal Peak Load Forecast | Base Zonal FRR Scaling Factor | FRR Portion of the Preliminary Peak Load Forecast | Preliminary Zonal Peak Load Forecast less FRR load
RTO | NA | NA | NA | 150313.4 | 153915 | NA | 12200.6 | 141714.4
AE | 1140 | >1311 | > 115% | 2460 | 2368 | 0.9626 | 0 | 2368
AEP | -170 | * | * | 22320 | 22313 | 0.99969 | 11305.7 | 11007.3
APS | 2020 | >2323 | > 115% | 8440 | 8617 | 1.021 | 0 | 8617
ATSI | 4660 | 9889 | 212.2% | 12660 | 12508 | 0.98799 | 0 | 12508
ATSI-CLEVELAND | 3540 | 5605 | 158.3% | NA | 4185.2 | NA | 0 | 4185.2
BGE | 4410 | 6244 | 141.6% | 6330 | 6566 | 1.0373 | 0 | 6566
COMED | 640 | 4064 | 635% | 20560 | 21589 | 1.05 | 0 | 21589
DAYTON | 2550 | 3401 | 133.4% | 3270 | 3305 | 1.0107 | 0 | 3305
DEOK | 3650 | 5072 | 139% | 5020 | 5343 | 1.0643 | 875.5 | 4467.5
DLCO | 1530 | >1760 | > 115% | 2750 | 2771 | 1.0076 | 0 | 2771
DOM | -3010 | * | * | 18450 | 19428 | 1.053 | 0 | 19428
DPL | 910 | >1047 | > 115% | 3740 | 3844 | 1.0278 | 0 | 3844
DPL SOUTH | 1230 | 1872 | 152.2% | NA | 2237.6 | NA | 0 | 2237.6
EKPC | 560 | >644 | > 115% | 2108.4 | 2132 | 1.0112 | 19.4 | 2112.6
JCPL | 3430 | >3945 | > 115% | 5650 | 5815 | 1.0292 | 0 | 5815
METED | 770 | >886 | > 115% | 2850 | 2865 | 1.0053 | 0 | 2865
PECO | 2690 | >3094 | > 115% | 8120 | 8305 | 1.0228 | 0 | 8305
PENLC | -210 | * | * | 2770 | 2771 | 1.0004 | 0 | 2771
PEPCO | 1540 | 7625 | 495.1% | 6030 | 6278 | 1.0411 | 0 | 6278
PL (incl. UGI) | -1010 | 7084 | * | 6870 | 7071 | 1.0293 | 0 | 7071
PS | 5900 | 8001 | 135.6% | 9530 | 9641 | 1.0116 | 0 | 9641
PS NORTH | 2620 | 4264 | 162.7% | NA | 4808 | NA | 0 | 4808
RECO | NA | NA | NA | 385 | 385 | 1 | 0 | 385
EMAAC | 3650 | 8800 | 241.1% | NA | 30358 | NA | 0
SWMAAC | 2900 | 9802 | 338% | NA | 12844 | NA | 0
Western MAAC | -10140 | * | * | NA | 12707 | NA | 0
MAAC | -7000 | 4218 | * | NA | 55909 | NA | 0
Western PJM | 2350 | >2703 | > 115% | NA | 78578 | NA | 12200.6
* LDA has adequate internal resources to meet the reliability criterion.
Limiting conditions at the CETL for modeled LDAs:
LDA | Violation/Limiting Facility
MAAC | Thermal/Sandy Spring "2334" - High Ridge 230 kV for loss of Sandy Spring "2314" - Burtonsville 230 kV
EMAAC | Voltage/Low Voltage at Cochranville 230 kV for loss of Keeney - Rock Springs 500 kV; low voltage at Hopatcong & Roseland 500 kV for loss of Branchburg - Hopatcong 500 kV
SWMAAC | Thermal/Graceton - Bagley 230 kV CKT #1 and #2 for the loss of the one or the other
PS | Thermal/Voltage/Roseland - Cedar Grove 230 kV for loss of Roseland - Williams Pipeline 230 kV/ Low voltage at Hopatcong & Roseland 500 kV for loss of Branchburg - Hopatcong 500 kV
PSNORTH | Thermal/Voltage/Roseland - Cedar Grove 230 kV for loss of Roseland - Williams Pipeline 230 kV/ Low voltage at Hopatcong & Roseland 500 kV for loss of Branchburg - Hopatcong 500 kV
DPLSOUTH | Thermal/Red Lion - Cedar Creek 230 kV for the loss of Cartanza - Milford 230 kV
PEPCO | Voltage/Voltage drop at High Ridge 230 kV station for the loss of Burches Hill - Possum Point 500 kV line
ATSI | Thermal/South Canton - Harmon 345kV line for the loss of the Hanna - Canton Central 345kV line
ATSI-CLEVELAND | Voltage/Low Voltage at Hayes for the loss of the Hayes - Davis Besse 345kV line
COMED | Thermal/Eugene - Dequin 345kV line for the loss of the Greentown - Jefferson 765kV line
BGE | Thermal/Pumphrey - Howard 230 kV line pre-contingency (Basecase)
PL | Thermal/Wescosville 500/138 kV transformer pre-contingency (Basecase)
DAYTON | Thermal/Sugar Creek - OHH 138 kV line for loss of OHH - College Corner 138 kV
DEOK | Thermal/Tanner - Miami Fort 345 kV line for the loss of the Terminal - South Bend 345 kV line
Planning Parameters initially posted on 2/1/2017. Updated on 2/13/2017: Limiting facilities updated for BGE, PL, DAYTON, and DEOK; PL CETL revised from 8285 MW to 7,226 MW; Added s1106 to the Key Transmission Upgrades. Updated on 4/13/2017: Added FRR load adjustments; updated CETL values for all LDAs except PEPCO and ATSI-Cleveland (and updated Limiting Facilitites for LDAs where applicable); updated CETO and Reliability Requirement for DAYTON LDA. Updated 5/9/2017: VRR Curve updated to reflect adjustments for total quantity of EE Resources for which PJM accepted an EE M&V Plan submitted for the auction. Updated 5/23/2017: Updated EE Add-backs to reflect cleared EE MW quantity of first-pass BRA solution times the threshold in accordance with Section 2.4.5 of Manual 18. Updated DEOK Reliability Requirement to adjust for FRR Minimum Internal Resource Requirement. Added Post-Auction Credit Rates for cleared resources.

## Net CONE
RPM CONE and E&AS Values for 2020/2021 Base Residual Auction
ICAP to UCAP Conversion Factor:
UCAP Price = ICAP Price / (1 - Pool-Wide Average EFORd)
Pool-Wide Average EFORd for 2020/2021 |  |  |  | 6.59%
CONE Area 1: AE, DPL, JCPL, PECO, PS, RECO
CONE Area 2: BGE, PEPCO
CONE Area 3: AEP, APS, ATSI, ComEd, Dayton, DEOK, Dominion, Duquesne (DLCo), EKPC
CONE Area 4: MetEd, Penelec, PPL
Zone/LDA | 2019/2020 BRA CONE: Levelized Revenue Requirement, $/MW-Year | BLS Composite Index: 2015/2014 Escalation | 2020/2021 BRA CONE: Levelized Revenue Requirement, $/MW-Year | Gross CONE, $/MW-Day, UCAP Price | Historic (2014-2016) Net Energy Revenue Offset, $/MW-Year | Ancillary Services Offset, $/MW-Year per Tariff | Net CONE, $/MW-Day, ICAP Price | Net CONE, $/MW-Day, UCAP Price | LDA Modeled with VRR Curve
CONE Area 1 | 133332.1198 | 1.0073 | 134309.8704 | 393.93
AE |  |  |  | 393.93 | 29791 | 2199 | 280.3284 | 300.11
DPL |  |  |  | 393.93 | 45179 | 2199 | 238.1695 | 254.97 | DPL SOUTH
JCPL |  |  |  | 393.93 | 42785 | 2199 | 244.7284 | 261.99
PE |  |  |  | 393.93 | 39239 | 2199 | 254.4435 | 272.39
PSEG |  |  |  | 393.93 | 27469 | 2199 | 286.6901 | 306.92 | PS, PSEG NORTH
RECO |  |  |  | 393.93 | 29070 | 2199 | 282.3038 | 302.22
EMAAC |  |  |  | 393.93 |  |  | 264.44 | 283.1 | EMAAC
CONE Area 2 | 134299.0885 | 1.0181 | 136733.0664 | 401.04
BGE |  |  |  | 401.04 | 73732 | 2199 | 166.581 | 178.33 | BGE
PEPCO |  |  |  | 401.04 | 57299 | 2199 | 211.6029 | 226.53 | PEPCO
SWMAAC |  |  |  | 401.04 |  |  | 189.09 | 202.43 | SWMAAC
CONE Area 4 | 134310.9379 | 0.9937 | 133464.6641 | 391.45
METED |  |  |  | 391.45 | 40581 | 2199 | 248.4511 | 265.98
PENELEC |  |  |  | 391.45 | 83670 | 2199 | 130.3991 | 139.6
PPL |  |  |  | 391.45 | 40121 | 2199 | 249.7114 | 267.33 | PPL
MAAC |  |  |  | 394.55 |  |  | 235.77 | 252.4 | MAAC
CONE Area 3 | 132664.7723 | 1.0056 | 133413.296 | 391.3
AEP |  |  |  | 391.3 | 35572 | 2199 | 262.0337 | 280.52
APS |  |  |  | 391.3 | 47208 | 2199 | 230.1542 | 246.39
ATSI |  |  |  | 391.3 | 42168 | 2199 | 243.9625 | 261.17 | ATSI, ATSI CLEVELAND
COMED |  |  |  | 391.3 | 18768 | 2199 | 308.072 | 329.81 | COMED
DAYTON |  |  |  | 391.3 | 38088 | 2199 | 255.1405 | 273.14 | DAYTON
DEOK |  |  |  | 391.3 | 34910 | 2199 | 263.8474 | 282.46 | DEOK
DLCO |  |  |  | 391.3 | 33774 | 2199 | 266.9597 | 285.79
DOM |  |  |  | 391.3 | 30025 | 2199 | 277.2309 | 296.79
EKPC |  |  |  | 391.3 | 30296 | 2199 | 276.4885 | 295.99
RTO | 133651.7296 |  | 134480.2242 | 394.43 | 32402 | 2199 | 273.6417 | 292.95 | RTO

## Key Transmission Upgrades
New Key Transmission Upgrades included for 2020/2021 Model
Upgrade ID | Description | Transmission Owner
b2668 | Reconductor Dequine - Meadow Lake 345 kV circuit #1 utilizing dual 954 ACSR 54/7 cardinal conductor | AEP
b2729 | Optimal Capacitors Configuration: New 175 MVAR 230 kV capacitor bank at Brambleton substation, new 175 MVAR 230 kV capacitor bank at Ashburn substation, new 300 MVAR 230 kV capacitor bank at Shelhorn substation, new 150 MVAR 230 kV capacitor bank at Liber | Dominion
b2732.1 | Cut-in of line 93505 Tazewell - Kendall 345 kV line into Dresden | ComEd
b2732.2 | Raise towers to remove the sag limitations on 345 kV line 8012 Pontiac - Loretto | ComEd
b2743.1 | Tap the Conemaugh - Hunterstown 500 kV line & create new Rice 500 kV & 230 kV stations. Install two 500/230 kV transformers, operated together. | Transource
b2743.2 | Tie in new Rice substation to Conemaugh-Hunterstown 500 kV | PENELEC
b2743.5 | Build new 230 kV double circuit line between Rice and Ringgold 230 kV, operated as a single circuit. | Transource
b2744 | Rebuild the Carson - Rogers Rd 500 kV circuit | Dominion
b2745 | Rebuild 21.32 miles of existing line between Chesterfield - Lakeside 230 kV | Dominion
b2752.1 | Tap the Peach Bottom – TMI 500 kV line & create new Furnace Run 500 kV & 230 kV stations. Install two 500/230 kV transformers, operated together. | Transource
b2752.2 | Tie in new Furnace Run substation to Peach Bottom-TMI 500 kV | PECO
b2752.5 | Build new 230 kV double circuit line between Furnace Run and Conastone 230 kV, operated as a single circuit. | Transource
b2752.7 | Reconductor/Rebuild the two Conastone - Northwest 230 kV lines and upgrade terminal equipment on both ends | BGE
n4906 | Upgrade the wire drops to the high side circuit switcher. Change the tap settings on the Pumphrey breakers B31 & B32 current transformers to correspond to 3000 amps and adjust relays to accommodate. Reset 6 additional relays and change out an auxiliary | BGE
s0866 | Build a new 230 kV circuit from Martins Creek to Monroe using existing Martins Creek-Stroudsburg 69 kV decommissioned line, and reconfigure Martins Creek and Monroe substations | PPL
s1101 | Rebuild the existing Shawnee-Bushkill 230 kV line (Approximately 2.2 Miles). | PPL
s1141 | Loop in the Meadow Lake - Olive 345 kV circuit into NIPSCo's Reynolds 765/345 kV station | AEP
s1143 | Add second circuit to approximately 23.7 miles of the Susquehanna-Jenkins 230 kV line using 1590 ACSR conductor | PPL
s1106 | Build new 500-230 kV Substation and associated transmission work (tap Sunbury - Susquehanna 500 kV and Colombia - Frackville 230 kV). | PPL
Key Transmission Upgrades included for 2019/2020 model but not included for 2020/2021 model
Upgrade ID | Description | Transmission Owner
None